## Intro
Technology Data for heating installations, Updated chapters - August 2016
Revised Marts 2018
This file contains the technology data sheets related to the updated technology data catalogue from August 2016 and revised December 2017. The following chapters are updated:
1 Oil-fired boiler
2 Natural gas boiler
3 District heating substation
1. Indirect substation
2. Direct substation
4 Biomass boilers, automatic stoking
5 Biomass boiler, manual stoking
6 Wood stove
7 Electric heat pumps
Air-to-air, existing one family house
Air-to-air, new one family house
Air-to-water, existing one family house
Air-to-water, new one family house
Air-to-water, existing apartments
Air-to-water, new apartments
Brine-to-water (ground source), existing one family house
Brine-to-water (ground source), new one family house
Brine-to-water (ground source), existing apartments
Brine-to-water (ground source), new apartments
Ventilation, new one family house
Ventilation, new apartments
8 Gas heat pumps
Gas driven absorption heat pumps, existing one family house (air-to-water and brine-to-water)
Gas driven absorption heat pumps, existing apartment complex (air-to-water and brine-to-water)
Gas engine driven heat pump, existing apartment complex (air-to-water and brine-to-water)
Gas driven adsorption heat pumps , existing one family house (brine-to-water)
15 Solar heating
16 Electric heating
17 SOFC mCHP - natural gas & biogas
18 LT-PEMFC mCHP - hydrogen
19 LT-PEMFC mCHP - natural gas

## 201 Oil-fired boiler
| Technology | Oil boiler (mineral oil fired, < 10 % FAME) - One-family house, existing and energy renovated buildings | [9 empty] | Technology | Oil boiler (bio oil) - One-family house, new building. HVO is assumed from 2030 | [9 empty] | Technology | Oil boiler (mineral oil fired, < 10 % FAME) - Apartment complex, existing building. | [9 empty] | Technology | Oil boiler (bio oil) - Apartment complex, new building. HVO is assumed from 2030
|  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref |  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref |  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref |  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper |  |  | Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper |  |  | Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper |  |  | Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
| Heat production capacity for one unit (kW) | 15 | 15 | 15 | 15 | 13 | 30 | 15 | 30 | A |  | Heat production capacity for one unit (kW) | 15 | 15 | 15 | 15 | 13 | 30 | 15 | 30 | A,I |  | Heat production capacity for one unit (kW) | 400 | 400 | 400 | 400 | 100 | 1000 | 100 | 1000 |  |  | Heat production capacity for one unit (kW) | 160 | 160 | 160 | 160 | 100 | 1000 | 100 | 1000
| Electricity generation capacity for one unit (kW) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | Electricity generation capacity for one unit (kW) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | Electricity generation capacity for one unit (kW) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | Electricity generation capacity for one unit (kW) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Expected share of space heating demand covered by unit (%) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  |  | Expected share of space heating demand covered by unit (%) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | I |  | Expected share of space heating demand covered by unit (%) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  |  | Expected share of space heating demand covered by unit (%) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
| Expected share of hot tap water demand covered by unit (%) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  |  | Expected share of hot tap water demand covered by unit (%) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | I |  | Expected share of hot tap water demand covered by unit (%) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  |  | Expected share of hot tap water demand covered by unit (%) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
| Electric efficiency, annual average, net (%) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | Electric efficiency, annual average, net (%) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | Electric efficiency, annual average, net (%) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | Electric efficiency, annual average, net (%) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Heat efficiency, annual average, net (%) | 92 | 92 | 93 | 95 | 90 | 95 | 95 | 98 | N | 1,2,3,4,14 | Heat efficiency, annual average, net (%) | 88 | 88 | 92 | 94 | 85 | 95 | 90 | 98 | G,N | 1,2,3,4,14 | Heat efficiency, annual average, net (%) | 92 | 92 | 93 | 95 | 90 | 95 | 95 | 98 | N | 1,2,3,4,14 | Heat efficiency, annual average, net (%) | 88 | 88 | 92 | 94 | 85 | 95 | 90 | 98 | G,N | 1,2,3,4,14
| Total efficiency, annual average, net (%) | 92 | 92 | 93 | 95 | 90 | 95 | 95 | 98 | N | 1,2,3,4,14 | Total efficiency, annual average, net (%) | 88 | 88 | 92 | 94 | 85 | 95 | 90 | 98 | G,N | 1,2,3,4,14 | Total efficiency, annual average, net (%) | 92 | 92 | 93 | 95 | 90 | 95 | 95 | 98 | N | 1,2,3,4,14 | Total efficiency, annual average, net (%) | 88 | 88 | 92 | 94 | 85 | 95 | 90 | 98 | G,N | 1,2,3,4,14
| Auxiliary Electricity consumption (kWh/year) | 150 | 140 | 130 | 110 | 100 | 160 | 90 | 150 | M | 11 | Auxiliary Electricity consumption (kWh/year) | 100 | 95 | 90 | 75 | 75 | 125 | 60 | 100 | M | 11 | Auxiliary Electricity consumption (kWh/year) | 1500 | 1400 | 1300 | 1200 | 1000 | 1800 | 500 | 1500 | M | 11 | Auxiliary Electricity consumption (kWh/year) | 1000 | 900 | 520 | 480 | 400 | 720 | 200 | 600 |  | 11
| Technical lifetime (years) | 20 | 20 | 20 | 20 | 15 | 25 | 15 | 25 |  |  | Technical lifetime (years) | 20 | 20 | 20 | 20 | 15 | 25 | 15 | 25 |  |  | Technical lifetime (years) | 20 | 20 | 20 | 20 | 15 | 25 | 15 | 25 |  |  | Technical lifetime (years) | 20 | 20 | 20 | 20 | 15 | 25 | 15 | 25
| Regulation ability | [10 empty] | Regulation ability | [10 empty] | Regulation ability | [10 empty] | Regulation ability
| Primary regulation (% per 30 seconds) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | Primary regulation (% per 30 seconds) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | Primary regulation (% per 30 seconds) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | Primary regulation (% per 30 seconds) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Secondary regulation (% per minute) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | Secondary regulation (% per minute) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | Secondary regulation (% per minute) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | Secondary regulation (% per minute) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Minimum load (% of full load) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Minimum load (% of full load) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Minimum load (% of full load) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Minimum load (% of full load) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Warm start-up time (hours) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Warm start-up time (hours) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Warm start-up time (hours) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Warm start-up time (hours) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cold start-up time (hours) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Cold start-up time (hours) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Cold start-up time (hours) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Cold start-up time (hours) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Environment | [10 empty] | Environment | [10 empty] | Environment | [10 empty] | Environment
| SO2 (g per GJ fuel) | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 1 | 0 | 1 | B,E |  | SO2 (g per GJ fuel) | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 1 | 0 | 1 | B,E |  | SO2 (g per GJ fuel) | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 1 | 0 | 1 | B,E |  | SO2 (g per GJ fuel) | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 1 | 0 | 1 | B,E
| NOX (g per GJ fuel) | 30 | 25 | 20 | 15 | 20 | 30 | 0 | 25 | C | 5 | NOX (g per GJ fuel) | 30 | 25 | 20 | 15 | 20 | 30 | 0 | 25 | C | 7 | NOX (g per GJ fuel) | 30 | 25 | 20 | 15 | 20 | 30 | 0 | 25 | C | 5 | NOX (g per GJ fuel) | 40 | 25 | 20 | 15 | 20 | 30 | 0 | 25 | C | 7
| CH4 (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | CH4 (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | CH4 (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | CH4 (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| N2O (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | N2O (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | N2O (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | N2O (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Particles (g per GJ fuel) | 0.03 | 0.02 | 0.01 | 0.01 | 0.01 | 0.03 | 0 | 0.02 | D |  | Particles (g per GJ fuel) | 0.03 | 0.02 | 0.01 | 0.01 | 0.01 | 0.03 | 0 | 0.02 | D |  | Particles (g per GJ fuel) | 0.03 | 0.02 | 0.01 | 0.01 | 0.01 | 0.03 | 0 | 0.02 | D |  | Particles (g per GJ fuel) | 0.03 | 0.02 | 0.01 | 0.01 | 0.01 | 0.03 | 0 | 0.02 | D
| Financial data | [10 empty] | Financial data | [10 empty] | Financial data | [10 empty] | Financial data
| Specific investment (1000€/unit) | 6 | 5.8515 | 5.5654 | 5.0345 | 5 | 8 | 4 | 7 | F, H, J |  | Specific investment (1000€/unit) | 10 | 9.7525 | 9.2757 | 8.3909 | 8 | 10 | 6 | 9 | F,H,I,J,L |  | Specific investment (1000€/unit) | 35 | 34.1337 | 32.4649 | 29.3681 | 32 | 38 | 26 | 33 | F, H, K |  | Specific investment (1000€/unit) | 28 | 27.307 | 25.9719 | 23.4945 | 20 | 40 | 20 | 40 | F,H,K,L
| - hereof equipment (%) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  |  | - hereof equipment (%) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  |  | - hereof equipment (%) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  |  | - hereof equipment (%) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
| - hereof installation (%) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  |  | - hereof installation (%) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  |  | - hereof installation (%) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  |  | - hereof installation (%) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
| Possible additional specific investment (1000€/unit) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | Possible additional specific investment (1000€/unit) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | Possible additional specific investment (1000€/unit) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | Possible additional specific investment (1000€/unit) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Fixed O&M (€/unit/year) | 249.45 | 243.7197 | 235.7466 | 214.2513 | 206.9 | 311.04 | 190.53 | 267.55 |  |  | Fixed O&M (€/unit/year) | 246.3 | 240.6147 | 231.7066 | 210.1563 | 205.175 | 308.625 | 187.02 | 261.7 |  |  | Fixed O&M (€/unit/year) | 854.5 | 837.7891 | 836.2524 | 778.1073 | 669 | 1024.2 | 558.5 | 975.5 |  |  | Fixed O&M (€/unit/year) | 563 | 549.7244 | 516.3045 | 475.7043 | 527.6 | 1049.68 | 473.4 | 970.2
| - of which is electricity costs (€/unit/year) | 9.45 | 9.66 | 13.13 | 12.87 | 6.9 | 11.04 | 10.53 | 17.55 | M |  | - of which is electricity costs (€/unit/year) | 6.3 | 6.555 | 9.09 | 8.775 | 5.175 | 8.625 | 7.02 | 11.7 | M |  | - of which is electricity costs (€/unit/year) | 94.5 | 96.6 | 131.3 | 140.4 | 69 | 124.2 | 58.5 | 175.5 | M |  | - of which is electricity costs (€/unit/year) | 63 | 62.1 | 52.52 | 56.16 | 27.6 | 49.68 | 23.4 | 70.2 | M
| - of which is other O&M costs (€/unit/year) | 240 | 234.0597 | 222.6166 | 201.3813 | 200 | 300 | 180 | 250 | H |  | - of which is other O&M costs (€/unit/year) | 240 | 234.0597 | 222.6166 | 201.3813 | 200 | 300 | 180 | 250 | H |  | - of which is other O&M costs (€/unit/year) | 760 | 741.1891 | 704.9524 | 637.7073 | 600 | 900 | 500 | 800 | H |  | - of which is other O&M costs (€/unit/year) | 500 | 487.6244 | 463.7845 | 419.5443 | 500 | 1000 | 450 | 900 | H
| Variable O&M (€/MWh) at 15-40 kW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Variable O&M (€/MWh) at 15-40 kW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Variable O&M (€/MWh) | 25.2 | 24.5763 | 23.3747 | 21.145 | 20 | 30 | 15 | 30 |  |  | Variable O&M (€/MWh) | 25.2 | 24.5763 | 23.3747 | 21.145 | 20 | 30 | 15 | 30
| Technology specific data | [10 empty] | Technology specific data | [10 empty] | Technology specific data | [10 empty] | Technology specific data
References:
1 | Study "Eco-design of Boilers and Combi-boilers http://www.ecoboiler.org/ . 2006-2007 by Van Holsteijn en Kemna (VHK) for the European Commission, DG Transport and Energy (DG TREN).
2 | RECENT PROGRESS (AND APPLICATION) ACHIEVED IN THE WAY TO ESTIMATE REAL PERFORMANCES OF DOMESTIC BOILERS ONCE INSTALLED Jean Schweitzer, Christian Holm Christiansen Danish Gas Technology Centre, Denmark Martin Koot Gastec, Holland Otto Paulsen DTI, Denmark. SAVE Workshop Utrecht 2000.
3 | BOILSIM http://www.boilsim.com/.2011
4 | Sparolie.dk with a list of high efficiency oil-fired boilers and with a list of the status for existing oilfired boilers.2011
5 | http://www.blauer-engel.de/_downloads/publikationen/erfolgsbilanz/ Erfolgsbilanz_Heiztechnologien.pdf (Rules for NOX). This is not present at the Blauer Engel Homepage, but can be found at the Internet.2011
7 | Rapsolie til opvarmning,Teknik, økonomi og miljø. Videncentret for biomasse 2001.
11 | Paulsen, O.: Calculation of electricity consumption of small oil and gasfired boilers – based on Laboratory test data. Annex F in Schweitzer, Jean: SAVE report 2005: http://www.boilerinfo.org/infosystem_el/webelproject/wp_reports/WP1.pdf.
14 | Kedeleffektiviteter for oliefyr og naturgaskedler i enfamiliehuse. DTU BYG, Teknologisk institut, Dansk Gasteknisk Center A/S, 2005
Notes:
A | The minimum heat output for a pressure atomisation burner is in the range of 13 kW. Due to the insignificant economy of scale displayed by domestic boilers (se section on economy of scale) the savings achieved by reducing the capacity below 13 kW is limited or non-existing. Hence, the investment cost is not influenced by the capacity of the boilers installed.
B | Domestic fuel oil can be desulphoried to the lower than 10 ppm Sulpur
C | The last limit for Nox for Blaue Engel were 110 mg/kWh. The value is based on this. In Practise the value can be lower. In 2050 is assumed flue gas cleaning for Nox
D | Based on Soot number 0 - 1, which is the average value in DK
E | Data for Sulphur content can be found at the homepages for the oile companies
F | Installation and service prices given by Weishaupt, Denmark 2011
G | Burners for liqued raw biofuel is not suited for condensing boilers for different reasons. In the case HVO becomes feasible condensing technology will work well
H | Assuming a cost-reduction of 0.5 % p.a., which in turn is assumed equivalent to the typical improvement of mature technologies.
I | New single family houses will have a heat demand at 2- 4 kW for space heating and a power demand for hot water at 32 kW. Using
a hot water tank the power need can go down to 0,5 kW depending on tank size. A typical compromise is a boiler at 20 kW and a tank at 80 liters.
J | Exchanging an oilfired boiler without changing the domestic hot water tank is normally not relevant. The price includes a tank.
K | The price does not include the domestic hot water system
L | The price includes a chimney/exhaust system
M | The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2015: 63, 2020: 69, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
N | The typical efficiency is believed to be approx. 5 %-point lower than the Eco-design label cf. ref [12]

## 202 Natural gas boiler
| Technology | Natural gas boiler - One-family house, existing and energy renovated buildings | [9 empty] | Technology | Natural gas boiler - One-family house, new buildings | [9 empty] | Technology | Natural gas boiler - Apartment complex, existing building | [9 empty] | Technology | Natural gas boiler - Apartment complex, new building
|  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref |  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref |  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref |  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper |  |  | Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper |  |  | Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper |  |  | Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
| Heat production capacity for one unit (kW) | 10 | 10 | 10 | 10 | 5 | 35 | 5 | 35 | U |  | Heat production capacity for one unit (kW) | 10 | 10 | 10 | 10 | 5 | 35 | 5 | 35 | U |  | Heat production capacity for one unit (kW) | 400 | 400 | 400 | 400 | 70 | 750 | 70 | 750 |  |  | Heat production capacity for one unit (kW) | 160 | 160 | 160 | 160 | 35 | 500 | 35 | 500
| Electricity generation capacity for one unit (kW) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | Electricity generation capacity for one unit (kW) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | Electricity generation capacity for one unit (kW) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | Electricity generation capacity for one unit (kW) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Expected share of space heating demand covered by unit (%) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  |  | Expected share of space heating demand covered by unit (%) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  |  | Expected share of space heating demand covered by unit (%) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  |  | Expected share of space heating demand covered by unit (%) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
| Expected share of hot tap water demand covered by unit (%) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  |  | Expected share of hot tap water demand covered by unit (%) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  |  | Expected share of hot tap water demand covered by unit (%) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  |  | Expected share of hot tap water demand covered by unit (%) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
| Electric efficiency, annual average, net (%) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | Electric efficiency, annual average, net (%) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | Electric efficiency, annual average, net (%) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | Electric efficiency, annual average, net (%) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Heat efficiency, annual average, net (%) | 97 | 97 | 98 | 99 | 95 | 100 | 98 | 102 | A, B | 1.28 | Heat efficiency, annual average, net (%) | 95 | 95 | 96 | 97 | 92 | 100 | 95 | 102 | A, B | 1.28 | Heat efficiency, annual average, net (%) | 101 | 101 | 102 | 102 | 99 | 103 | 100 | 104 | A,B,L,O,P,M | 30, 31 | Heat efficiency, annual average, net (%) | 101 | 101 | 102 | 102 | 99 | 103 | 100 | 104 | A,B,L,O,P,M | 30, 31
| Total efficiency, annual average, net (%) | 97 | 97 | 98 | 99 | 95 | 100 | 98 | 102 | A, B | 1 | Total efficiency, annual average, net (%) | 95 | 95 | 96 | 97 | 92 | 100 | 95 | 102 | A, B | 1 | Total efficiency, annual average, net (%) | 101 | 101 | 102 | 102 | 99 | 103 | 100 | 104 | A,B,L,O,P,M | 30, 31 | Total efficiency, annual average, net (%) | 101 | 101 | 102 | 102 | 99 | 103 | 100 | 104 | A,B,L,O,P,M | 30, 31
| Auxiliary Electricity consumption (kWh/year) | 150 | 140 | 130 | 110 | 100 | 160 | 90 | 150 | T | 28 | Auxiliary Electricity consumption (kWh/year) | 80 | 75 | 70 | 50 | 60 | 100 | 40 | 80 | T | 28 | Auxiliary Electricity consumption (kWh/year) | 750 | 700 | 600 | 500 | 500 | 1000 | 250 | 750 | T,M | 30 | Auxiliary Electricity consumption (kWh/year) | 375 | 350 | 300 | 250 | 250 | 500 | 200 | 400 | T,M | 30
| Technical lifetime (years) | 20 | 20 | 20 | 20 | 15 | 25 | 15 | 25 |  | 2 | Technical lifetime (years) | 20 | 20 | 20 | 20 | 15 | 25 | 15 | 25 |  | 2 | Technical lifetime (years) | 25 | 25 | 25 | 25 | 20 | 30 | 20 | 30 | M | 31 | Technical lifetime (years) | 25 | 25 | 25 | 25 | 20 | 30 | 20 | 30 | M | 31
| Regulation ability | [10 empty] | Regulation ability | [10 empty] | Regulation ability | [10 empty] | Regulation ability
| Primary regulation (% per 30 seconds) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | L |  | Primary regulation (% per 30 seconds) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | L |  | Primary regulation (% per 30 seconds) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | L |  | Primary regulation (% per 30 seconds) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | L
| Secondary regulation (% per minute) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | L |  | Secondary regulation (% per minute) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | L |  | Secondary regulation (% per minute) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | L |  | Secondary regulation (% per minute) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | L
| Minimum load (% of full load) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | L |  | Minimum load (% of full load) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | L |  | Minimum load (% of full load) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | L |  | Minimum load (% of full load) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | L
| Warm start-up time (hours) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | L |  | Warm start-up time (hours) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | L |  | Warm start-up time (hours) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | L |  | Warm start-up time (hours) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | L
| Cold start-up time (hours) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | L |  | Cold start-up time (hours) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | L |  | Cold start-up time (hours) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | L |  | Cold start-up time (hours) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | L
| Environment | [10 empty] | Environment | [10 empty] | Environment | [10 empty] | Environment
| SO2 (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0.3 | 0 | 0.3 |  | 5 | SO2 (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0.3 | 0 | 0.3 |  | 5 | SO2 (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0.3 | 0 | 0.3 | N | 5 | SO2 (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0.3 | 0 | 0.3 | N | 5
| NOX (g per GJ fuel) | 20 | 10 | 5 | 3 | 5 | 15 | 0.2 | 0.3 | D, E | 3.7 | NOX (g per GJ fuel) | 20 | 10 | 5 | 3 | 5 | 15 | 0.2 | 0.3 | D, E | 3.7 | NOX (g per GJ fuel) | 20 | 10 | 5 | 3 | 5 | 15 | 0.2 | 0.3 | N | 3.7 | NOX (g per GJ fuel) | 20 | 10 | 5 | 3 | 5 | 15 | 0.2 | 0.3 | N | 3.7
| CH4 (g per GJ fuel) | 2 | 1 | 0.5 | 0.25 | 0.5 | 2 | 0.1 | 0.5 | F | 5 | CH4 (g per GJ fuel) | 2 | 1 | 0.5 | 0.25 | 0.5 | 2 | 0.1 | 0.5 | F | 5 | CH4 (g per GJ fuel) | 2 | 1 | 0.5 | 0.25 | 0.5 | 2 | 0.1 | 0.5 | F,N | 5 | CH4 (g per GJ fuel) | 2 | 1 | 0.5 | 0.25 | 0.5 | 2 | 0.1 | 0.5 | F,N | 5
| N2O (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 |  |  | N2O (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 |  |  | N2O (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | N |  | N2O (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | N
| Particles (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0.1 |  |  | Particles (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0.1 |  |  | Particles (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0.1 | N |  | Particles (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0.1 | N
| Financial data | [10 empty] | Financial data | [10 empty] | Financial data | [10 empty] | Financial data
| Specific investment (1000€/unit) | 3.2 | 3.1208 | 2.9682 | 2.6851 | 3 | 4.5 | 2.5 | 4 | G, H, I | 32 | Specific investment (1000€/unit) | 3.2 | 3.1208 | 2.9682 | 2.6851 | 3 | 4.5 | 2.5 | 4.5 | C, G, H, I | 32 | Specific investment (1000€/unit) | 25.2 | 24.5763 | 23.3747 | 21.145 | 20 | 30 | 16 | 26 | C, O, P, R |  | Specific investment (1000€/unit) | 18 | 17.5545 | 16.6962 | 15.1036 | 15 | 20 | 12 | 18 | C, O, P, R
| - hereof equipment (%) | 63 | 63 | 63 | 63 | 50 | 75 | 50 | 75 |  |  | - hereof equipment (%) | 63 | 63 | 63 | 63 | 50 | 75 | 50 | 75 |  |  | - hereof equipment (%) | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | H |  | - hereof equipment (%) | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | H
| - hereof installation (%) | 37 | 37 | 37 | 37 | 25 | 50 | 25 | 50 |  |  | - hereof installation (%) | 37 | 37 | 37 | 37 | 25 | 50 | 25 | 50 |  |  | - hereof installation (%) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  |  | - hereof installation (%) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
| Possible additional specific investment (1000€/unit) | 2 | 1.9505 | 1.8551 | 1.6782 | 1 | 3 | 1 | 3 | K | 6 | Possible additional specific investment (1000€/unit) | 2 | 1.9505 | 1.8551 | 1.6782 | 1 | 3 | 1 | 3 | K | 6 | Possible additional specific investment (1000€/unit) | 2 | 1.9505 | 1.8551 | 1.6782 | 1 | 3 | 1 | 3 | C, J | 6 | Possible additional specific investment (1000€/unit) | 2 | 1.9505 | 1.8551 | 1.6782 | 1 | 3 | 1 | 3 | C, J | 6
| Fixed O&M (€/unit/year) | 209.45 | 204.7098 | 198.6438 | 180.6877 | 186.9 | 261.04 | 140.53 | 217.55 |  |  | Fixed O&M (€/unit/year) | 209.45 | 204.7098 | 198.6438 | 180.6877 | 186.9 | 261.04 | 140.53 | 217.55 |  |  | Fixed O&M (€/unit/year) | 683.25 | 669.3 | 650.6 | 619.5 | 531.3 | 814.2 | 478.05 | 760.95 |  |  | Fixed O&M (€/unit/year) | 447.625 | 438.15 | 424.3 | 403.25 | 348.45 | 531.3 | 322.6 | 495.6
| - of which is electricity costs (€/unit/year) | 9.45 | 9.66 | 13.13 | 12.87 | 6.9 | 11.04 | 10.53 | 17.55 | T |  | - of which is electricity costs (€/unit/year) | 9.45 | 9.66 | 13.13 | 12.87 | 6.9 | 11.04 | 10.53 | 17.55 | T |  | - of which is electricity costs (€/unit/year) | 47.25 | 48.3 | 60.6 | 58.5 | 34.5 | 69 | 29.25 | 87.75 | T |  | - of which is electricity costs (€/unit/year) | 23.625 | 24.15 | 30.3 | 29.25 | 17.25 | 34.5 | 23.4 | 46.8 | T
| - of which is other O&M costs (€/unit/year) | 200 | 195.0498 | 185.5138 | 167.8177 | 180 | 250 | 130 | 200 | J | 33 | - of which is other O&M costs (€/unit/year) | 200 | 195.0498 | 185.5138 | 167.8177 | 180 | 250 | 130 | 200 | J | 33 | - of which is other O&M costs (€/unit/year) | 636 | 621 | 590 | 561 | 496.8 | 745.2 | 448.8 | 673.2 | C, O, P, R, S |  | - of which is other O&M costs (€/unit/year) | 424 | 414 | 394 | 374 | 331.2 | 496.8 | 299.2 | 448.8 | C, O, P, R, S
| Variable O&M (€/MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Variable O&M (€/MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Variable O&M (€/MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Q |  | Variable O&M (€/MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Q
| Technology specific data | [10 empty] | Technology specific data | [10 empty] | Technology specific data | [10 empty] | Technology specific data
References:
1 | Annual efficiency calculation method for domestic boilers. SAVE Contract XVII/4.1031/93-008.
2 | Gaskedlers naturlige overlevelse, Gasenergi nr. 5 2015,
3 | Study "Ecodesign of Boilers and Combi-boilers" (VHK) for the European Commission, DG Transport and Energy (DG TREN). Task 4 Section 3.1.
5 | Start stop emissions of domestic appliances. H. Hüppelshäuser and F. Jansen. Ruhrgas. IGRC 1998.
6 | HMN: http://salg.naturgas.dk.
7 | DGC project : Evaluation of the NOx emissions of the Danish population of gas boilers below 120 kW
28 | Facts and figures about domestic gas boilers. A compilation of results covering 25 years of testing at DGC's laboratory. DGC February 2016
29 | Drift- og vedligeholdelsesomkostninger for små gaskedler (villakedler), HMN GasNet, 2016
30 | DGC Statistics, Efficiency and Emission test reports from district heating plants, up to and including 2014
31 | Danish District Heating Association, information given to the 2012 survey for the report
32 | Installation costs of new condensing gas boilers in NGF Nature Energys distribution area from 2012 - 2015, NGF Nature Energy (in Danish: Priser for installation af ny kondenserende gaskedel i Nature Energys distributionsområde i perioden 2012-2015)
33 | Operation and maintenance costs of small gas boilers, HMN GasNet 2016 (in Danish: Drift- og vedligeholdelsesomkostninger for små gaskedler (villakedler)
Notes:
A | Annual efficiency calculated with input test data carried out at DGC and using the model BOILSIM for the BAT [1].
B | A slight improvement of efficiency is still possible over the next decades is assumed
C | Assuming a cost-reduction of 0.5 % p.a., which in turn is assumed equivalent to the typical improvement of mature technologies.
D | Ecodesign limit for gas boilers = 70 mg/kWh = 70/3.6 = approx. 20 g/GJ fuel.
E | NOx emission will decrease as an average. The level proposed for 2030 is already achievable today by some gas boilers.
F | Ref [5] gives 5 mg/kWh, This is less than 2 g/GJ.
G | All costs are based on Naturgas Fyn (today “Nature Energy”) statistics. This is the most extensive data base indicating real costs paid by the customer including installation. The value given does not include the energy saving incentive funds that are given to the client for the purchase of a condensing boiler (3000 DKK = 400 Euro).
H | Assuming a cost-reduction of 0.5 % p.a., which in turn is assumed equivalent to the typical improvement of mature technologies. The harmonisation of gas quality in EU, the more severe competition with district heating and electrical heat pumps, and the improvements in the manufacturing cost are the reason for such hypothesis. The statistics of Naturgas Fyn (today "NGF Nature Energy") shows that the costs have already decreased between 2012 and 2015.
I | The “uncertainty” was based on Naturgas Fyn (today “Nature Energy”) statistics removing 5% at top and 5% at bottom list of the total cost. Additional uncertainties like labour cost variations in Denmark may add some more uncertainty in the prices given.
J | HMN GasNets database contains comprehensive statistical data.
K | Installation of a gas service line (grid connection). The price may change depending on the marketing by the gas distribution companies. For non-domestic appliances, the same price as for domestic is assumed. Only to be paid if the natural gas is not yet supplied to the house. Lifetime for the branchpipe is estimated to be 50 years.
L | Gas boilers can deliver their full power in a few seconds or few minutes depending on the heat capacity of the appliance and possible pre-purge time. The same applies for the modulating ability within the modulation range of the boiler according to ref. [7]
M | The technical performance of an apartment complex boiler is considered to be very similar to that of a district heating boiler with the exception of more frequent start-ups and shutdowns. Consequently the efficiency is reduced accordingly.
N | The emissions are assumed to be very similar to the ones for domestic boilers. This is believed to be a conservative estimate.
O | Based on a 160 kW boiler (new building) and 400 kW (existing building)
P | Based on average cost information from manufacturers (2015).
Q | There are no statistics on variable O&M for large boilers, and the cost can very well be included in the service agreement. The estimates from manufacturers are quite low and, therefore, the variable O&M costs for large boilers is considered to be included in the Fixed O&M.
R | Uncertainty +/- 20%
S | Service cost interpolated from manufacturers information (2015)
T | The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2015: 63, 2020: 69, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
U | Due to the insignificant economy of scale displayed by domestic boilers (se section on economy of scale) the savings achieved by reducing the capacity of the boilers is limited or non-existing. Hence, the investment cost is not influenced by the capacity of the boilers installed.

## 203.1 Indirect DH subst
| Technology | Indirect district heating substation - One-family house, existing and energy renovated buildings | [9 empty] | Technology | Indirect district heating substation - One-family house new buildings | [9 empty] | Technology | Indirect district heating substation - Apartment complex, existing building | [9 empty] | Technology | Indirect district heating substation - Apartment complex, new building
|  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref |  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref |  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref |  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper |  |  | Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper |  |  | Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper |  |  | Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
| Heat production capacity for one unit (kW) | 10 | 10 | 10 | 10 | 5 | 15 | 5 | 15 | H |  | Heat production capacity for one unit (kW) | 10 | 10 | 10 | 10 | 5 | 15 | 5 | 15 | H |  | Heat production capacity for one unit (kW) | 400 | 400 | 400 | 400 | 150 | 500 | 150 | 500 | A |  | Heat production capacity for one unit (kW) | 160 | 160 | 160 | 160 | 150 | 500 | 150 | 500 | A
| Electricity generation capacity for one unit (kW) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | Electricity generation capacity for one unit (kW) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | Electricity generation capacity for one unit (kW) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | Electricity generation capacity for one unit (kW) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Expected share of space heating demand covered by unit (%) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  |  | Expected share of space heating demand covered by unit (%) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  |  | Expected share of space heating demand covered by unit (%) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  |  | Expected share of space heating demand covered by unit (%) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
| Expected share of hot tap water demand covered by unit (%) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  |  | Expected share of hot tap water demand covered by unit (%) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  |  | Expected share of hot tap water demand covered by unit (%) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  |  | Expected share of hot tap water demand covered by unit (%) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
| Electric efficiency, annual average, net (%) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | Electric efficiency, annual average, net (%) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | Electric efficiency, annual average, net (%) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | Electric efficiency, annual average, net (%) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Heat efficiency, annual average, net (%) | 97 | 98 | 98 | 98 | 95 | 99 | 95 | 99 | B, I | 9 | Heat efficiency, annual average, net (%) | 96 | 96 | 97 | 98 | 95 | 99 | 95 | 99 | B, I | 9 | Heat efficiency, annual average, net (%) | 100 | 100 | 100 | 100 | 98 | 100 | 98 | 100 | B, I |  | Heat efficiency, annual average, net (%) | 100 | 100 | 100 | 100 | 98 | 100 | 98 | 100 | B, I
| Total efficiency, annual average, net (%) | 97 | 98 | 98 | 98 | 95 | 99 | 95 | 99 |  |  | Total efficiency, annual average, net (%) | 96 | 96 | 97 | 98 | 95 | 99 | 95 | 99 |  |  | Total efficiency, annual average, net (%) | 100 | 100 | 100 | 100 | 98 | 100 | 98 | 100 |  |  | Total efficiency, annual average, net (%) | 100 | 100 | 100 | 100 | 98 | 100 | 98 | 100
| Auxiliary Electricity consumption (kWh/year) | 120 | 110 | 100 | 80 | 75 | 125 | 50 | 100 | G |  | Auxiliary Electricity consumption (kWh/year) | 60 | 55 | 50 | 40 | 40 | 80 | 25 | 75 | G |  | Auxiliary Electricity consumption (kWh/year) | 600 | 550 | 500 | 400 | 400 | 1000 | 250 | 800 | G |  | Auxiliary Electricity consumption (kWh/year) | 350 | 325 | 300 | 250 | 250 | 500 | 200 | 400 | G
| Technical lifetime (years) | 25 | 25 | 25 | 25 | 20 | 30 | 20 | 30 |  | 8 | Technical lifetime (years) | 25 | 25 | 25 | 25 | 20 | 30 | 20 | 30 |  | 8 | Technical lifetime (years) | 25 | 25 | 25 | 25 | 20 | 30 | 20 | 30 |  | 8 | Technical lifetime (years) | 25 | 25 | 25 | 25 | 20 | 30 | 20 | 30 |  | 8
| Regulation ability | [10 empty] | Regulation ability | [10 empty] | Regulation ability | [10 empty] | Regulation ability
| Primary regulation (% per 30 seconds) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | Primary regulation (% per 30 seconds) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | Primary regulation (% per 30 seconds) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | Primary regulation (% per 30 seconds) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Secondary regulation (% per minute) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | Secondary regulation (% per minute) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | Secondary regulation (% per minute) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | Secondary regulation (% per minute) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Minimum load (% of full load) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | Minimum load (% of full load) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | Minimum load (% of full load) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | Minimum load (% of full load) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Warm start-up time (hours) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | Warm start-up time (hours) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | Warm start-up time (hours) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | Warm start-up time (hours) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Cold start-up time (hours) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | Cold start-up time (hours) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | Cold start-up time (hours) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | Cold start-up time (hours) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Environment | [10 empty] | Environment | [10 empty] | Environment | [10 empty] | Environment
| SO2 (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | SO2 (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | SO2 (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | SO2 (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| NOX (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | NOX (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | NOX (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | NOX (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| CH4 (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | CH4 (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | CH4 (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | CH4 (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| N2O (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | N2O (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | N2O (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | N2O (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Particles (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | Particles (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | Particles (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | Particles (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Financial data | [10 empty] | Financial data | [10 empty] | Financial data | [10 empty] | Financial data
| Specific investment (1000€/unit) | 2.2 | 2.1455 | 2.0407 | 1.846 | 1 | 3 | 1 | 2.5 | F | 2,3,4,7 | Specific investment (1000€/unit) | 2.2 | 2.1455 | 2.0407 | 1.846 | 1 | 3 | 1 | 2.5 | F | 2,3,4,7 | Specific investment (1000€/unit) | 16 | 15.604 | 14.8411 | 13.4254 | 12 | 20 | 10 | 20 | F | 2,4,7 | Specific investment (1000€/unit) | 11.2 | 10.9228 | 10.3888 | 9.3978 | 10 | 15 | 8 | 12 | F | 2,4,7
| - hereof equipment (%) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  |  | - hereof equipment (%) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  |  | - hereof equipment (%) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  |  | - hereof equipment (%) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
| - hereof installation (%) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  |  | - hereof installation (%) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  |  | - hereof installation (%) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  |  | - hereof installation (%) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
| Possible additional specific investment (1000€/unit) | 3 | 2.9257 | 2.7827 | 2.5173 | 2 | 4 | 2 | 4 | C, F |  | Possible additional specific investment (1000€/unit) | 3 | 2.9257 | 2.7827 | 2.5173 | 2 | 4 | 2 | 4 | C, F |  | Possible additional specific investment (1000€/unit) | 4 | 3.901 | 3.7103 | 3.3564 | 3 | 6 | 3 | 6 | C, F |  | Possible additional specific investment (1000€/unit) | 4 | 3.901 | 3.7103 | 3.3564 | 3 | 6 | 3 | 6 | C, F
| Fixed O&M (€/unit/year) | 57.56 | 56.3524 | 56.4784 | 51.3144 | 40.175 | 73.625 | 35.85 | 71.7 |  |  | Fixed O&M (€/unit/year) | 53.78 | 52.5574 | 51.4284 | 46.6344 | 37.76 | 70.52 | 32.925 | 68.775 |  |  | Fixed O&M (€/unit/year) | 138.8 | 136.4501 | 144.1845 | 131.5479 | 107.6 | 189 | 94.25 | 198.6 |  |  | Fixed O&M (€/unit/year) | 107.05 | 105.3211 | 109.1434 | 100.5725 | 87.25 | 134.5 | 83.4 | 136.8
| - of which is electricity costs (€/unit/year) | 7.56 | 7.59 | 10.1 | 9.36 | 5.175 | 8.625 | 5.85 | 11.7 | G |  | - of which is electricity costs (€/unit/year) | 3.78 | 3.795 | 5.05 | 4.68 | 2.76 | 5.52 | 2.925 | 8.775 | G |  | - of which is electricity costs (€/unit/year) | 37.8 | 37.95 | 50.5 | 46.8 | 27.6 | 69 | 29.25 | 93.6 | G |  | - of which is electricity costs (€/unit/year) | 22.05 | 22.425 | 30.3 | 29.25 | 17.25 | 34.5 | 23.4 | 46.8 | G
| - of which is other O&M costs (€/unit/year) | 50 | 48.7624 | 46.3784 | 41.9544 | 35 | 65 | 30 | 60 | D, F | 8 | - of which is other O&M costs (€/unit/year) | 50 | 48.7624 | 46.3784 | 41.9544 | 35 | 65 | 30 | 60 | D, F | 8 | - of which is other O&M costs (€/unit/year) | 101 | 98.5001 | 93.6845 | 84.7479 | 80 | 120 | 65 | 105 | D, F | 8 | - of which is other O&M costs (€/unit/year) | 85 | 82.8961 | 78.8434 | 71.3225 | 70 | 100 | 60 | 90 | D, F | 8
| Variable O&M (€/MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Variable O&M (€/MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Variable O&M (€/MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Variable O&M (€/MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Technology specific data | [10 empty] | Technology specific data | [10 empty] | Technology specific data | [10 empty] | Technology specific data
References:
1 | Forslag til Forskrifter for godkendte standardunits, Teknologisk Institut, 2005.
2 | Communication with Gemina Termix, www.termix.dk. 2011
3 | Delrapport 2 - DEMONSTRATION AF LAVENERGIFJERNVARME TIL LAVENERGIBYGGERI I BOLIGFORENINGEN RINGGÅRDENS AFD. 34 I LYSTRUP. Ener-gistyrelsen - EUDP 2008-II, 2011.
4 | Communication with Danfoss Redan, www.redan.danfoss.com. Technology data for individual heat production and energy transport, 2011
5 | www.metrotherm.dk. 2011
6 | Krav til fjernvarmeunits I VarmeTransmission Aarhus, December 2011.
7 | Prices from different providers of substations, 2016
8 | Analysis conducted by COWI on the lifetime and operation and maintenance costs of district heating units, 2016
9 | Replacement of district heating unit, Danish Energy Agency, April 2017 (In Danish: Udskiftning af fjernvarmeunit, Videncenter for Energibesparelser i Bygninger under Energistyrelsen)
Notes:
A | The generating capacity for one substation is set at the space heating capacity at typical district heating flow/return temperatures of 70°C/40°C. The size of the water heater capacity is estimated based on the number of apartments that the substation can supply with space heating.
B | The only losses related to the district heating substation are the standby heat losses and system losses related to the cooling of the return flow. For large well-insulated substations, these are considered negligible – 100% efficiency. However, substations for single-family houses will have a heat loss during summer that cannot be considered useful. Applying best available technology, this is considered to be about 3%, resulting in 97% efficiency.
C | Specific investment in branch pipe from the steet network to the building and in the heat meter. Lifetime for the branchpipe is estimated to be 50 years.
D | The operation and maintenance costs are based on a maintenance check every second year, but calculated per year and per installation.
E | Note that the branch pipe should be dimensioned for the use of hot tap water. If there is not any hot water tank, the branch pipe capacity should be higher than the capacity of the DH substation.
F | Assuming a cost-reduction of 0.5 % p.a., which in turn is assumed equivalent to the typical improvement of mature technologies.
G | The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2015: 63, 2020: 69, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
H | Due to the insignificant economy of scale displayed by domestic district heating substations (se section on economy of scale) the savings achieved by reducing the capacity of the substation is limited or non-existing. Hence, the investment cost is not influenced by the capacity of the substations installed.
I | In contrast to boilers and heat pumps a district heating unit does not convert energy. Yet energy losses are still present in a district heating substation [9]. Some of these losses are included in the annual heat demand, while others are not. The efficiencies are calculated to reflect this.

## 203.2 Direct DH subst
| Technology | Direct district heating substation - One-family house, existing, new and energy renovated buildings | [9 empty] | Technology | Direct district heating substation - Apartment complex, existing building | [9 empty] | Technology | Direct district heating substation - Apartment complex, new building
|  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref |  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref |  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper |  |  | Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper |  |  | Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
| Heat production capacity for one unit (kW) | 10 | 10 | 10 | 10 | 5 | 15 | 5 | 15 | H |  | Heat production capacity for one unit (kW) | 400 | 400 | 400 | 400 | 150 | 500 | 150 | 500 | A |  | Heat production capacity for one unit (kW) | 160 | 160 | 160 | 160 | 150 | 500 | 150 | 500 | A
| Electricity generation capacity for one unit (kW) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | Electricity generation capacity for one unit (kW) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | Electricity generation capacity for one unit (kW) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Expected share of space heating demand covered by unit (%) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  |  | Expected share of space heating demand covered by unit (%) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  |  | Expected share of space heating demand covered by unit (%) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
| Expected share of hot tap water demand covered by unit (%) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  |  | Expected share of hot tap water demand covered by unit (%) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  |  | Expected share of hot tap water demand covered by unit (%) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
| Electric efficiency, annual average, net (%) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | Electric efficiency, annual average, net (%) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | Electric efficiency, annual average, net (%) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Heat efficiency, annual average, net (%) | 100 | 100 | 100 | 100 | 98 | 100 | 99 | 100 | I | 9 | Heat efficiency, annual average, net (%) | 100 | 100 | 100 | 100 | 98 | 100 | 99 | 100 | I |  | Heat efficiency, annual average, net (%) | 100 | 100 | 100 | 100 | 98 | 100 | 99 | 100 | I
| Total efficiency, annual average, net (%) | 100 | 100 | 100 | 100 | 98 | 100 | 99 | 100 |  |  | Total efficiency, annual average, net (%) | 100 | 100 | 100 | 100 | 98 | 100 | 99 | 100 |  |  | Total efficiency, annual average, net (%) | 100 | 100 | 100 | 100 | 98 | 100 | 99 | 100
| Auxiliary Electricity consumption (kWh/year) | 40 | 40 | 35 | 30 | 50 | 100 | 50 | 100 | G |  | Auxiliary Electricity consumption (kWh/year) | 200 | 200 | 175 | 150 | 150 | 300 | 125 | 250 | G |  | Auxiliary Electricity consumption (kWh/year) | 200 | 200 | 175 | 150 | 150 | 300 | 125 | 250 | G
| Technical lifetime (years) | 25 | 25 | 25 | 25 | 20 | 30 | 20 | 30 |  | 8 | Technical lifetime (years) | 25 | 25 | 25 | 25 | 20 | 30 | 20 | 30 |  | 8 | Technical lifetime (years) | 25 | 25 | 25 | 25 | 20 | 30 | 20 | 30 |  | 8
| Regulation ability | [10 empty] | Regulation ability | [10 empty] | Regulation ability
| Primary regulation (% per 30 seconds) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | Primary regulation (% per 30 seconds) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | Primary regulation (% per 30 seconds) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Secondary regulation (% per minute) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | Secondary regulation (% per minute) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | Secondary regulation (% per minute) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Minimum load (% of full load) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | Minimum load (% of full load) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | Minimum load (% of full load) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Warm start-up time (hours) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | Warm start-up time (hours) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | Warm start-up time (hours) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Cold start-up time (hours) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | Cold start-up time (hours) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | Cold start-up time (hours) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Environment | [10 empty] | Environment | [10 empty] | Environment
| SO2 (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | SO2 (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | SO2 (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| NOX (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | NOX (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | NOX (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| CH4 (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | CH4 (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | CH4 (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| N2O (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | N2O (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | N2O (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Particles (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | Particles (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | Particles (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Financial data | [10 empty] | Financial data | [10 empty] | Financial data
| Specific investment (1000€/unit) | 1.9 | 1.853 | 1.7624 | 1.5943 | 1 | 3 | 1 | 2.5 | F | 7 | Specific investment (1000€/unit) | 14 | 13.6535 | 12.986 | 11.7472 | 10 | 18 | 10 | 15 | F | 7 | Specific investment (1000€/unit) | 10 | 9.7525 | 9.2757 | 8.3909 | 8 | 12 | 7 | 10 | F | 7
| - hereof equipment (%) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  |  | - hereof equipment (%) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  |  | - hereof equipment (%) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
| - hereof installation (%) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  |  | - hereof installation (%) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  |  | - hereof installation (%) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
| Possible additional specific investment (1000€/unit) | 3 | 2.9257 | 2.7827 | 2.5173 | 2 | 4 | 2 | 4 | C, F |  | Possible additional specific investment (1000€/unit) | 4 | 3.901 | 3.7103 | 3.3564 | 3 | 6 | 3 | 6 | C, F |  | Possible additional specific investment (1000€/unit) | 4 | 3.901 | 3.7103 | 3.3564 | 3 | 6 | 3 | 6 | C, F
| Fixed O&M (€/unit/year) | 49.52 | 48.5967 | 47.1307 | 42.9472 | 38.45 | 66.9 | 35.85 | 61.7 |  |  | Fixed O&M (€/unit/year) | 89.6 | 88.8942 | 89.0978 | 82.1598 | 75.35 | 110.7 | 74.625 | 109.25 |  |  | Fixed O&M (€/unit/year) | 77.6 | 77.1912 | 77.967 | 72.0908 | 60.35 | 100.7 | 64.625 | 99.25
| - of which is electricity costs (€/unit/year) | 2.52 | 2.76 | 3.535 | 3.51 | 3.45 | 6.9 | 5.85 | 11.7 | J |  | - of which is electricity costs (€/unit/year) | 12.6 | 13.8 | 17.675 | 17.55 | 10.35 | 20.7 | 14.625 | 29.25 | J |  | - of which is electricity costs (€/unit/year) | 12.6 | 13.8 | 17.675 | 17.55 | 10.35 | 20.7 | 14.625 | 29.25 | J
| - of which is other O&M costs (€/unit/year) | 47 | 45.8367 | 43.5957 | 39.4372 | 35 | 60 | 30 | 50 | D, F | 8 | - of which is other O&M costs (€/unit/year) | 77 | 75.0942 | 71.4228 | 64.6098 | 65 | 90 | 60 | 80 | D, F | 8 | - of which is other O&M costs (€/unit/year) | 65 | 63.3912 | 60.292 | 54.5408 | 50 | 80 | 50 | 70 | D, F | 8
| Variable O&M (€/MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Variable O&M (€/MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Variable O&M (€/MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Technology specific data | [10 empty] | Technology specific data | [10 empty] | Technology specific data
References:
7 | Prices from different providers of substations, 2016
8 | Analysis conducted by COWI on the operation and maintenance costs of district heating units, 2016
9 | Replacement of district heating unit, Danish Energy Agency, April 2017 (In Danish: Udskiftning af fjernvarmeunit, Videncenter for Energibesparelser i Bygninger under Energistyrelsen)
Notes:
A | The generating capacity for one substation is set at the space heating capacity at typical district heating flow/return temperatures of 70°C/40°C. The size of the water heater capacity is estimated based on the number of apartments that the substation can supply with space heating.
C | Specific investment in branch pipe from the steet network to the building and in the heat meter. Lifetime for the branchpipe is estimated to be 50 years.
D | The operation and maintenance costs are based on a maintenance check every second year, but cal-culated per year and per installation.
E | Note that the branch pipe should be dimensioned for the use of hot tap water. If there is not any hot water tank, the branch pipe capacity should be higher than the capacity of the DH substation.
F | Assuming a cost-reduction of 0.5 % p.a., which in turn is assumed equivalent to the typical improvement of mature technologies.
G | The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2015: 63, 2020: 69, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
H | Due to the insignificant economy of scale displayed by domestic district heating substations (se section on economy of scale) the savings achieved by reducing the capacity of the substation is limited or non-existing. Hence, the investment cost is not influenced by the capacity of the substations installed.
I | In contrast to boilers and heat pumps a district heating unit does not convert energy. Yet energy losses are still present in a district heating substation [9]. Some of these losses are included in the annual heat demand, while others are not. The efficiencies are calculated to reflect this.

## 204 Biomass boiler, automatic
| Technology | Biomass boiler, automatic stoking , wood pellets or wood chips - One-family house, existing and energy renovated buildings. | [9 empty] | Technology | Biomass boiler, automatic stoking , wood pellets or wood chips - One-family house, new buildings. | [9 empty] | Technology | Biomass boiler, automatic stoking , wood pellets or wood chips - Apartment complex, existing building | [9 empty] | Technology | Biomass boiler, automatic stoking , wood pellets or wood chips - Apartment complex, new building
|  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref |  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref |  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref |  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper |  |  | Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper |  |  | Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper |  |  | Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
| Heat production capacity for one unit (kW) | 12 | 10 | 10 | 10 | 8 | 15 | 8 | 10 | A | 4 | Heat production capacity for one unit (kW) | 12 | 10 | 8 | 8 | 8 | 15 | 8 | 10 | A | 4 | Heat production capacity for one unit (kW) | 400 | 400 | 400 | 400 | 200 | 600 | 200 | 600 | A |  | Heat production capacity for one unit (kW) | 160 | 160 | 160 | 160 | 80 | 400 | 80 | 400 | A
| Electricity generation capacity for one unit (kW) | NA | NA | NA | NA | NA | NA | NA | NA |  |  | Electricity generation capacity for one unit (kW) | NA | NA | NA | NA | NA | NA | NA | NA |  |  | Electricity generation capacity for one unit (kW) | NA | NA | NA | NA | NA | NA | NA | NA | J | 7 | Electricity generation capacity for one unit (kW) | NA | NA | NA | NA | NA | NA | NA | NA | J | 7
| Expected share of space heating demand covered by unit (%) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  |  | Expected share of space heating demand covered by unit (%) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  |  | Expected share of space heating demand covered by unit (%) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  |  | Expected share of space heating demand covered by unit (%) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
| Expected share of hot tap water demand covered by unit (%) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  |  | Expected share of hot tap water demand covered by unit (%) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  |  | Expected share of hot tap water demand covered by unit (%) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  |  | Expected share of hot tap water demand covered by unit (%) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
| Electric efficiency, annual average, net (%) | NA | NA | NA | NA | NA | NA | NA | NA |  |  | Electric efficiency, annual average, net (%) | NA | NA | NA | NA | NA | NA | NA | NA |  |  | Electric efficiency, annual average, net (%) | NA | NA | NA | NA | NA | NA | NA | NA |  | 7 | Electric efficiency, annual average, net (%) | NA | NA | NA | NA | NA | NA | NA | NA |  | 7
| Heat efficiency, annual average, net (%) | 80 | 82 | 86 | 88 | 74.4846 | 89.5154 | 80.4846 | 95.5154 | G |  | Heat efficiency, annual average, net (%) | 75 | 78 | 80 | 85 | 70 | 85 | 80.4846 | 95.5154 | G |  | Heat efficiency, annual average, net (%) | 80 | 85 | 90 | 90 | 79.144 | 90.856 | 85.08 | 94.92 |  |  | Heat efficiency, annual average, net (%) | 80 | 85 | 90 | 90 | 79.144 | 90.856 | 85.08 | 94.92
| Total efficiency, annual average, net (%) | 80 | 82 | 86 | 88 | 74.4846 | 89.5154 | 80.4846 | 95.5154 | B | 5 | Total efficiency, annual average, net (%) | 75 | 78 | 80 | 85 | 70 | 85 | 80.4846 | 95.5154 | B | 5 | Total efficiency, annual average, net (%) | 80 | 85 | 90 | 90 | 79.144 | 90.856 | 85.08 | 94.92 | B | 5 | Total efficiency, annual average, net (%) | 80 | 85 | 90 | 90 | 79.144 | 90.856 | 85.08 | 94.92 | B | 5
| Auxiliary Electricity consumption (kWh/year) | 250 | 240 | 220 | 200 | 200 | 300 | 150 | 250 | O | 8 | Auxiliary Electricity consumption (kWh/year) | 200 | 190 | 180 | 160 | 175 | 250 | 150 | 200 | O | 8 | Auxiliary Electricity consumption (kWh/year) | 2500 | 2400 | 2200 | 2000 | 2200 | 3000 | 1800 | 2500 | O |  | Auxiliary Electricity consumption (kWh/year) | 1500 | 1400 | 1320 | 1250 | 1200 | 2000 | 1000 | 1800 | O
| Technical lifetime (years) | 20 | 20 | 20 | 20 | 15 | 25 | 15 | 25 |  | 7 | Technical lifetime (years) | 20 | 20 | 20 | 20 | 15 | 25 | 15 | 25 |  | 7 | Technical lifetime (years) | 20 | 20 | 20 | 20 | 15 | 25 | 15 | 25 |  | 6 | Technical lifetime (years) | 20 | 20 | 20 | 20 | 15 | 25 | 15 | 25 |  | 6
| Regulation ability | [10 empty] | Regulation ability | [10 empty] | Regulation ability | [10 empty] | Regulation ability
| Primary regulation (% per 30 seconds) | NA | NA | NA | NA | NA | NA | NA | NA |  |  | Primary regulation (% per 30 seconds) | NA | NA | NA | NA | NA | NA | NA | NA |  |  | Primary regulation (% per 30 seconds) | NA | NA | NA | NA | NA | NA | NA | NA |  |  | Primary regulation (% per 30 seconds) | NA | NA | NA | NA | NA | NA | NA | NA
| Secondary regulation (% per minute) | NA | NA | NA | NA | NA | NA | NA | NA |  |  | Secondary regulation (% per minute) | NA | NA | NA | NA | NA | NA | NA | NA |  |  | Secondary regulation (% per minute) | NA | NA | NA | NA | NA | NA | NA | NA |  |  | Secondary regulation (% per minute) | NA | NA | NA | NA | NA | NA | NA | NA
| Minimum load (% of full load) | NA | NA | NA | NA | NA | NA | NA | NA |  |  | Minimum load (% of full load) | NA | NA | NA | NA | NA | NA | NA | NA |  |  | Minimum load (% of full load) | NA | NA | NA | NA | NA | NA | NA | NA |  |  | Minimum load (% of full load) | NA | NA | NA | NA | NA | NA | NA | NA
| Warm start-up time (hours) | NA | NA | NA | NA | NA | NA | NA | NA |  |  | Warm start-up time (hours) | NA | NA | NA | NA | NA | NA | NA | NA |  |  | Warm start-up time (hours) | NA | NA | NA | NA | NA | NA | NA | NA |  |  | Warm start-up time (hours) | NA | NA | NA | NA | NA | NA | NA | NA
| Cold start-up time (hours) | NA | NA | NA | NA | NA | NA | NA | NA |  |  | Cold start-up time (hours) | NA | NA | NA | NA | NA | NA | NA | NA |  |  | Cold start-up time (hours) | NA | NA | NA | NA | NA | NA | NA | NA |  |  | Cold start-up time (hours) | NA | NA | NA | NA | NA | NA | NA | NA
| Environment | [10 empty] | Environment | [10 empty] | Environment | [10 empty] | Environment
| SO2 (g per GJ fuel) | 25 | 25 | 25 | 25 | 17.8986 | 32.1014 | 17.8986 | 32.1014 |  | 9 | SO2 (g per GJ fuel) | 25 | 25 | 25 | 25 | 17.8986 | 32.1014 | 17.8986 | 32.1014 |  | 9 | SO2 (g per GJ fuel) | 25 | 25 | 25 | 25 | 17.8986 | 32.1014 | 17.8986 | 32.1014 |  | 8 | SO2 (g per GJ fuel) | 25 | 25 | 25 | 25 | 17.8986 | 32.1014 | 17.8986 | 32.1014 |  | 8
| NOX (g per GJ fuel) | 90 | 70 | 50 | 40 | 62.4846 | 120 | 31.9657 | 48.0343 |  |  | NOX (g per GJ fuel) | 90 | 70 | 50 | 40 | 62.4846 | 120 | 31.9657 | 48.0343 |  |  | NOX (g per GJ fuel) | 90 | 70 | 50 | 40 | 62.4846 | 120 | 31.9657 | 48.0343 |  | 5 | NOX (g per GJ fuel) | 90 | 70 | 50 | 40 | 62.4846 | 120 | 31.9657 | 48.0343 |  | 5
| CH4 (g per GJ fuel) | 3 | 2 | 1 | 0 | -0.296 | 4.296 | 0 | 2 |  |  | CH4 (g per GJ fuel) | 3 | 2 | 1 | 0 | -0.296 | 4.296 | 0 | 2 |  |  | CH4 (g per GJ fuel) | 3 | 2 | 1 | 0 | -0.296 | 4.296 | 0 | 2 |  | 2,5 | CH4 (g per GJ fuel) | 3 | 2 | 1 | 0 | -0.296 | 4.296 | 0 | 2 |  | 2.5
| N2O (g per GJ fuel) | 4 | 4 | 4 | 4 | 0.78627 | 7.2137 | 0.78627 | 7.2137 |  | 9 | N2O (g per GJ fuel) | 4 | 4 | 4 | 4 | 0.78627 | 7.2137 | 0.78627 | 7.2137 |  | 9 | N2O (g per GJ fuel) | 4 | 4 | 4 | 4 | 0.78627 | 7.2137 | 0.78627 | 7.2137 |  | 8 | N2O (g per GJ fuel) | 4 | 4 | 4 | 4 | 0.78627 | 7.2137 | 0.78627 | 7.2137 |  | 8
| Particles (g per GJ fuel) | 19 | 15 | 12 | 10 | 9.144 | 20.856 | 5.08 | 14.92 | C | 4 | Particles (g per GJ fuel) | 19 | 15 | 12 | 10 | 9.144 | 20.856 | 5.08 | 14.92 | C | 4 | Particles (g per GJ fuel) | 19 | 15 | 12 | 10 | 9.144 | 20.856 | 5.08 | 14.92 | C |  | Particles (g per GJ fuel) | 19 | 15 | 12 | 10 | 9.144 | 20.856 | 5.08 | 14.92 | C
| Financial data | [10 empty] | Financial data | [10 empty] | Financial data | [10 empty] | Financial data
| Specific investment (1000€/unit) | 7 | 6.8267 | 6.493 | 5.8736 | 2.5 | 11 | 2 | 10 | F, L |  | Specific investment (1000€/unit) | 7 | 6.8267 | 6.493 | 5.8736 | 2.5 | 11 | 2 | 10 | F, L |  | Specific investment (1000€/unit) | 90 | 87.7724 | 83.4812 | 75.518 | 80.257 | 95.2878 | 68.0026 | 83.0334 | K, L, M |  | Specific investment (1000€/unit) | 54 | 52.6634 | 50.0887 | 45.3108 | 45.148 | 60.1789 | 37.7954 | 52.8262 | K, L, M | 6
| - hereof equipment (%) | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  |  | - hereof equipment (%) | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 5 | - hereof equipment (%) | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  |  | - hereof equipment (%) | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
| - hereof installation (%) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 5 | - hereof installation (%) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 5 | - hereof installation (%) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  |  | - hereof installation (%) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
| Possible additional specific investment (1000€/unit) | 1.6 | 1.5604 | 1.4841 | 1.3425 | 1.5 | 2 | 1.2 | 1.8 | D, E, L |  | Possible additional specific investment (1000€/unit) | 1.3 | 1.2678 | 1.2058 | 1.0908 | 1.1 | 1.5 | 1 | 1.3 | D, E, L |  | Possible additional specific investment (1000€/unit) | 15 | 14.6287 | 13.9135 | 12.5863 | 7.1133 | 22.1442 | 5.0709 | 20.1018 | H, L |  | Possible additional specific investment (1000€/unit) | 9 | 8.7772 | 8.3481 | 7.5518 | 1.2618 | 16.2927 | 0.036373 | 15.0672 | H, L
| Fixed O&M (€/unit/year) | 515.75 | 504.1844 | 486.0045 | 442.9443 | 413.8 | 570.7 | 367.55 | 529.25 |  |  | Fixed O&M (€/unit/year) | 512.6 | 500.7344 | 481.9645 | 438.2643 | 412.075 | 567.25 | 367.55 | 523.4 |  |  | Fixed O&M (€/unit/year) | 1757.5 | 1725.998 | 1706.3104 | 1576.5418 | 1151.8 | 2407 | 1010.6 | 2192.5 |  |  | Fixed O&M (€/unit/year) | 1154.5 | 1130.3637 | 1116.5431 | 1035.6839 | 882.8 | 1538 | 717 | 1410.6
| - of which is electricity costs (€/unit/year) | 15.75 | 16.56 | 22.22 | 23.4 | 13.8 | 20.7 | 17.55 | 29.25 | N |  | - of which is electricity costs (€/unit/year) | 12.6 | 13.11 | 18.18 | 18.72 | 12.075 | 17.25 | 17.55 | 23.4 | N |  | - of which is electricity costs (€/unit/year) | 157.5 | 165.6 | 222.2 | 234 | 151.8 | 207 | 210.6 | 292.5 | N |  | - of which is electricity costs (€/unit/year) | 94.5 | 96.6 | 133.32 | 146.25 | 82.8 | 138 | 117 | 210.6 | N
| - of which is other O&M costs (€/unit/year) | 500 | 487.6244 | 463.7845 | 419.5443 | 400 | 550 | 350 | 500 | L | 11 | Fixed O&M (€/unit/year) | 500 | 487.6244 | 463.7845 | 419.5443 | 400 | 550 | 350 | 500 | L | 11 | Fixed O&M (€/unit/year) | 1600 | 1560.398 | 1484.1104 | 1342.5418 | 1000 | 2200 | 800 | 1900 | I, L | 11 | Fixed O&M (€/unit/year) | 1060 | 1033.7637 | 983.2231 | 889.4339 | 800 | 1400 | 600 | 1200 | I, L | 11
| Variable O&M (€/MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Variable O&M (€/MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Variable O&M (€/MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Variable O&M (€/MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Technology specific data | [10 empty] | Technology specific data | [10 empty] | Technology specific data | [10 empty] | Technology specific data
References:
2 | Emissioner fra træfyrede brændeovne og -kedler, Miljøprojekt nr. 1324 2010, Johnny Iversen, Thomas Capral Henriksen og Simon Dreyer, Carl Bro.
4 | www.teknologisk.dk/911; Listen over godkendte biobrændselsanlæg.
5 | Strategic Research and Innovation Agenda for Renewable Heating & Cooling; RHC-Platform 2013; Renewable heating & Cooling; European Technology Platform.
6 | Energibesparelser - det behøver ikke være så svært; Energibranchen.dk, nr. 3, september 2009.
7 | Lot 15: Solid fuel small combustion installations-Base Case definition.
8 | Konvertering fra olie og el til fast biobrændsel; 2012; Videncenter for Energibesparelser
9 | Danish Emission Inventories for stationary combustion plants, inventories until 2011, Scientific Report from DCE n0. 102, 2014
11 | Estimate by the Danish Energy Agency and Energinet, 2017
Notes:
A | Nominal heat delivered in 2015 from 10-20 kW in single family houses and 100 – 500 kW in apartment complexes. Regarding small units (20 kW and less) the insignificant economy of scale displayed by domestic boilers (se section on economy of scale) the savings achieved by reducing the capacity of the boiler is limited or non-existing. Hence, the investment cost is not influenced by the capacity of the boiler installed.
B | Efficiency development from [5]
C | EN303-5 measurement method
D | Prerequisite: house with central heating system.
E | Chimney
F | Difference in price (2015) 2.5-11 (1000€/unit) mainly due to finish, design etc.
G | Improved real life conditions for flue gas condensation technology will increase the efficiency to >100% (based on NCV).
H | Biomass storage
I | Contemporary value from [6]
J | If production of electricity then ORC
K | Boilers for production of heat only
L | Assuming a cost-reduction of 0.5 % p.a., which in turn is assumed equivalent to the typical improvement of mature technologies.
M | The cost is based on a unit with a capacity of 200 kW and assuming the cost for this unit is equally split between an initial cost and a linear dependence on the capacity of the unit.
N | The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2015: 63, 2020: 69, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.

## 205 Biomass boiler, manual
| Technology | Biomass boiler, manual stoking, wood logs - One-family house, existing, new and energy renovated buildings
|  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
| Heat production capacity for one unit (kW) | 35 | 30 | 25 | 25 | 25 | 35 | 20 | 35 | A | 4
| Electricity generation capacity for one unit (kW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Expected share of space heating demand covered by unit (%) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
| Expected share of hot tap water demand covered by unit (%) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
| Electric efficiency, annual average, net (%) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat efficiency, annual average, net (%) | 80 | 82 | 86 | 88 | 70 | 89.5154 | 80.4846 | 95.5154
| Total efficiency, annual average, net (%) | 80 | 82 | 86 | 88 | 70 | 89.5154 | 80.4846 | 95.5154 |  | 5
| Auxiliary Electricity consumption (kWh/year) | 250 | 240 | 220 | 200 | 200 | 300 | 150 | 250 | G | 8
| Technical lifetime (years) | 20 | 20 | 20 | 20 | 15 | 25 | 15 | 25 |  | 7
Regulation ability
| Primary regulation (% per 30 seconds) | NA | NA | NA | NA | NA | NA | NA | NA
| Secondary regulation (% per minute) | NA | NA | NA | NA | NA | NA | NA | NA
| Minimum load (% of full load) | NA | NA | NA | NA | NA | NA | NA | NA
| Warm start-up time (hours) | NA | NA | NA | NA | NA | NA | NA | NA
| Cold start-up time (hours) | NA | NA | NA | NA | NA | NA | NA | NA
Environment
| SO2 (g per GJ fuel) | 25 | 25 | 25 | 25 | 17.8986 | 32.1014 | 17.8986 | 32.1014 |  | 9
| NOX (g per GJ fuel) | 80 | 70 | 60 | 50 | 62.4846 | 120 | 41.8 | 58.2 |  | 5
| CH4 (g per GJ fuel) | 3 | 2 | 1 | 0 | -0.296 | 4.296 | 0 | 2 |  | 2.5
| N2O (g per GJ fuel) | 4 | 4 | 4 | 4 | 0.78627 | 7.2137 | 0.78627 | 7.2137 |  | 9
| Particles (g per GJ fuel) | 150 | 120 | 95 | 60 | 100 | 140 | 50 | 70 | C | 9
Financial data
| Specific investment (1000€/unit) | 7 | 6.8267 | 6.493 | 5.8736 | 5 | 14 | 4 | 12 | F
| - hereof equipment (%) | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
| - hereof installation (%) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
| Possible additional specific investment (1000€/unit) | 3.1 | 3.0233 | 2.8755 | 2.6012 | 3 | 2.6 | 2.4 | 4 | B, D, E, F
| Fixed O&M (€/unit/year) | 465.75 | 455.4219 | 439.626 | 400.9899 | 363.8 | 520.7 | 317.55 | 479.25
| - of which is electricity costs (€/unit/year) | 15.75 | 16.56 | 22.22 | 23.4 | 13.8 | 20.7 | 17.55 | 29.25 | G
| - of which is other O&M costs (€/unit/year) | 450 | 438.8619 | 417.406 | 377.5899 | 350 | 500 | 300 | 450 | F | 11
| Variable O&M (€/MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Technology specific data
References:
2 | Emissioner fra træfyrede brændeovne og -kedler, Miljøprojekt nr. 1324 2010, Johnny Iversen, Thomas Capral Henriksen og Simon Dreyer, Carl Bro.
4 | www.teknologisk.dk/911; Listen over godkendte biobrændselsanlæg.
5 | Strategic Research and Innovation Agenda for Renewable Heating & Cooling; RHC-Platform 2013; Renewable heating & Cooling; European Technology Platform.
7 | Lot 15: Solid fuel small combustion installations-Base Case definition.
8 | Konvertering fra olie og el til fast biobrændsel; 2012; Videncenter for Energibesparelser
9 | Danish Emission Inventories for stationary combustion plants, inventories until 2011, Scientific Report from DCE n0. 102, 2014
11 | Estimate by the Danish Energy Agency and Energinet, 2017
Notes:
A | Nominal heat delivery in 2015 from 30-40 kW.
B | Storage tank.
C | EN303-5 measurement method.
D | Prerequisite: house with central heating system.
E | Chimney.
F | Assuming a cost-reduction of 0.5 % p.a., which in turn is assumed equivalent to the typical improvement of mature technologies.
G | The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2015: 63, 2020: 69, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.

## 206 Wood stove
| Technology | Wood stove without water tank, wood logs - One-family house, existing, energy renovated and new buildings | [9 empty] | Technology | Wood stove with water tank - One-family house, existing, energy renovated and new buildings
|  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref |  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper |  |  | Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
| Heat production capacity for one unit (kW) | 6 | 5 | 4 | 4 | 4 | 8 | 4 | 8 | F |  | Heat production capacity for one unit (kW) | 15 | 12 | 10 | 10 | 10 | 15 | 8 | 12
| Electricity generation capacity for one unit (kW) | NA | NA | NA | NA | NA | NA | NA | NA |  |  | Electricity generation capacity for one unit (kW) | NA | NA | NA | NA | NA | NA | NA | NA
| Expected share of space heating demand covered by unit (%) | 40 | 40 | 40 | 40 | 20 | 60 | 20 | 60 | C |  | Expected share of space heating demand covered by unit (%) | 45 | 45 | 45 | 45 | 20 | 70 | 20 | 70 | C
| Expected share of hot tap water demand covered by unit (%) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E |  | Expected share of hot tap water demand covered by unit (%) | 20 | 20 | 20 | 20 | 10 | 40 | 10 | 40 | E
| Electric efficiency, annual average, net (%) | NA | NA | NA | NA | NA | NA | NA | NA |  |  | Electric efficiency, annual average, net (%) | NA | NA | NA | NA | NA | NA | NA | NA
| Heat efficiency, annual average, net (%) | 65 | 70 | 75 | 75 | 62.4846 | 77.5154 | 67.4846 | 82.5154 |  |  | Heat efficiency, annual average, net (%) | 65 | 70 | 75 | 75 | 62.4846 | 77.5154 | 67.4846 | 82.5154
| Total efficiency, annual average, net (%) | 65 | 70 | 75 | 75 | 62.4846 | 77.5154 | 67.4846 | 82.5154 |  |  | Total efficiency, annual average, net (%) | 65 | 70 | 75 | 75 | 62.4846 | 77.5154 | 67.4846 | 82.5154
| Auxiliary Electricity consumption (kWh/year) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Auxiliary Electricity consumption (kWh/year) | 150 | 140 | 130 | 110 | 100 | 160 | 90 | 150 | H
| Technical lifetime (years) | 20 | 20 | 20 | 20 | 15 | 25 | 15 | 25 |  | 2 | Technical lifetime (years) | 20 | 20 | 20 | 20 | 15 | 25 | 15 | 25 |  | 2
| Regulation ability | [10 empty] | Regulation ability
| Primary regulation (% per 30 seconds) | NA | NA | NA | NA | NA | NA | NA | NA |  |  | Primary regulation (% per 30 seconds) | NA | NA | NA | NA | NA | NA | NA | NA
| Secondary regulation (% per minute) | NA | NA | NA | NA | NA | NA | NA | NA |  |  | Secondary regulation (% per minute) | NA | NA | NA | NA | NA | NA | NA | NA
| Minimum load (% of full load) | NA | NA | NA | NA | NA | NA | NA | NA |  |  | Minimum load (% of full load) | NA | NA | NA | NA | NA | NA | NA | NA
| Warm start-up time (hours) | NA | NA | NA | NA | NA | NA | NA | NA |  |  | Warm start-up time (hours) | NA | NA | NA | NA | NA | NA | NA | NA
| Cold start-up time (hours) | NA | NA | NA | NA | NA | NA | NA | NA |  |  | Cold start-up time (hours) | NA | NA | NA | NA | NA | NA | NA | NA
| Environment | [10 empty] | Environment
| SO2 (g per GJ fuel) | 25 | 25 | 25 | 25 | 17.8986 | 32.1014 | 17.8986 | 32.1014 |  | 3 | SO2 (g per GJ fuel) | 25 | 25 | 25 | 25 | 17.8986 | 32.1014 | 17.8986 | 32.1014 |  | 3
| NOX (g per GJ fuel) | 90 | 90 | 90 | 90 | 85.08 | 120 | 85.08 | 120 |  |  | NOX (g per GJ fuel) | 90 | 90 | 90 | 90 | 85.08 | 120 | 85.08 | 120
| CH4 (g per GJ fuel) | 320 | 125 | 100 | 100 | 100 | 300 | 50 | 200 |  | 1.3 | CH4 (g per GJ fuel) | 320 | 125 | 100 | 100 | 100 | 300 | 50 | 200 |  | 1,3
| N2O (g per GJ fuel) | 4 | 4 | 4 | 4 | 0.78627 | 7.2137 | 0.78627 | 7.2137 |  | 3 | N2O (g per GJ fuel) | 4 | 4 | 4 | 4 | 0.78627 | 7.2137 | 0.78627 | 7.2137 |  | 3
| Particles (g per GJ fuel) | 50 | 40 | 30 | 25 | 25 | 250 | 15 | 200 | A | 1 | Particles (g per GJ fuel) | 50 | 40 | 30 | 25 | 25 | 150 | 15 | 100 | A | 1
| Financial data | [10 empty] | Financial data
| Specific investment (1000€/unit) | 2.5 | 2.5 | 3.5 | 3.1 | 2 | 3 | 2.5 | 4 | D | 2 | Specific investment (1000€/unit) | 4 | 4 | 4.5 | 4.2 | 3 | 5 | 3.5 | 5.5 | D | 2
| - hereof equipment (%) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 2 | - hereof equipment (%) | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 |  | 2
| - hereof installation (%) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2 | - hereof installation (%) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 2
| Possible additional specific investment (1000€/unit) | 1.6 | 1.5604 | 1.4841 | 1.3425 | 1.5 | 2 | 1.2 | 1.8 | B, G |  | Possible additional specific investment (1000€/unit) | 1.6 | 1.5604 | 1.4841 | 1.3425 | 1.5 | 2 | 1.2 | 1.8 | B, G
| Fixed O&M (€/unit/year) | 150 | 145 | 200 | 190 | 125 | 200 | 150 | 250 |  |  | Fixed O&M (€/unit/year) | 209.45 | 204.66 | 263.13 | 252.87 | 156.9 | 261.04 | 160.53 | 267.55
| - of which is electricity costs (€/unit/year) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | - of which is electricity costs (€/unit/year) | 9.45 | 9.66 | 13.13 | 12.87 | 6.9 | 11.04 | 10.53 | 17.55 | H
| - of which is other O&M costs (€/unit/year) | 150 | 145 | 200 | 190 | 125 | 200 | 150 | 250 | D | 6 | - of which is other O&M costs (€/unit/year) | 200 | 195 | 250 | 240 | 150 | 250 | 150 | 250 | D | 6
| Variable O&M (€/MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Variable O&M (€/MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Technology specific data | [10 empty] | Technology specific data
References:
1 | Emissioner fra træfyrede brændeovne og -kedler, Miljøprojekt nr. 1324 2010, Johnny Iversen, Thomas Capral Henriksen og Simon Dreyer, Carl Bro.
2 | Lot 15: Solid fuel small combustion installations-Base Case definition.
3 | Danish Emission Inventories for stationary combustion plants, inventories until 2011, Scientific Report from DCE n0. 102, 2014
6 | Estimate by the Danish Energy Agency and Energinet, 2017
Notes:
A | DIN Plus measurement method.
B | Chimney.
C | The share of space heating covered by a wood stove depends on the possibility to regularly charge the stove with wood logs and of the location of the stove in the house. With regularly charging and a central location of the stove, the coverage can be up to 80 % of the heating demand in the house. Approximately 10 % larger is possible for stoves with a water tank. Taking into consideration that normally the average residents will have difficulties with regular fuel charging, the expected share of space heating covered by the wood stove without a water tank will be in the range of 20 % to 60 %.
D | More automatic stoves are expected in the future(2030) Therefor an increment in investment is expected. After these periods, it is expected that the technology becomes generic and therefor investment is expected to drop as the technology becomes cheaper., while still assuming a cost-reduction of 0.5 % p.a., which in turn is assumed equivalent to the typical improvement of mature technologies.
E | Only for stoves with water tank, otherwise 0%.
F | Nominal heat delivery in 2015 from 4-12 kW.
G | Assuming a cost-reduction of 0.5 % p.a., which in turn is assumed equivalent to the typical improvement of mature technologies.
H | The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2015: 63, 2020: 69, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.

## 207.1 Air to air existing
| Technology | Heat pump, Air-to-air, existing one family house
| Energy/technical data | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
[6 empty] | Lower | Upper | Lower | Upper
| Heat production capacity for one unit (kW) | 4 | 4 | 6 | 6 | 2 | 10 | 2 | 10 |  | 1,2,5
| Electricity generation capacity for one unit (kW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Expected share of space heating demand covered by unit (%) | 60 | 60 | 60 | 60 | 50 | 70 | 40 | 80 | F | 1,2,7
| Expected share of hot tap water demand covered by unit (%) | 0 | 0 | 100 | 100 | 0 | 100 | 0 | 100 | F | 1.2
| Heat efficiency, annual average, net (%) | 500 | 510 | 410 | 420 | 400 | 550 | 350 | 600 | C, H, I | 4,5,7,8
| Total efficiency, annual average, net (%) | 500 | 510 | 410 | 420 | 400 | 550 | 350 | 600 | C, H, J | 4,5,7,8
| Auxiliary Electricity consumption (kWh/year) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Technical lifetime (years) | 12 | 12 | 12 | 12 | 10 | 15 | 10 | 15
Regulation ability
| Change in capacity within 1 minute (%) | 100 | 100 | 100 | 100 | 50 | 100 | 50 | 100 |  | 1,2,7
| Warm start-up time (hours) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1,2,7
| Cold start-up time (hours) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1,2,7
Environment
| SO2 (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| NOX (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| CH4 (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| N2O (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Particles (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Financial data
| Specific investment (1000€/unit) | 1.8 | 1.7 | 1.9 | 1.8 | 1.4 | 2 | 1.2 | 2 | K | 1,2,3,14
| - hereof equipment (%) | 85 | 85 | 75 | 75 | 60 | 90 | 60 | 90 |  | 1,2,7
| - hereof installation (%) | 15 | 15 | 25 | 25 | 10 | 40 | 10 | 40 |  | 1,2,7
Possible additional specific investment (1000€/unit)
| Fixed O&M (€/unit/year) | 170 | 161.6683 | 146.2099 | 132.263 | 150 | 250 | 100 | 150
| Variable O&M (€/MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1,2,7
References:
1 | Danfoss, 2015, information provided at workshop
2 | Bosch, 2015 , information provided at workshop
3 | Market and Statistics Report, EHPA 2014
5 | Energistyrelsen, 2015, conversation
7 | Teknologisk Institut, 2015, conversation
8 | Godkendelse af tilskudsberettigede anlæg, måling, dataindsamling og formidling, Teknologisk Institut 2013
14 | Heat implementation scenarios until 2030, Ecofys 2013
Notes:
C | Weighted by seasonal heat demand of average climate zones according to EN14825 and domestic hot water production according to EN16147
F | The share of heating demand and hot tap water demand covered depends on how the heat pump is operated in the total heat energy system in the house.
H | The reason for the drop in COP values in 2030 and 2050, is hot tap water production from 2030 and onwards
I | Heat efficiency values refers to the COP of the heat pump
J | Total efficiency values are including auxilliary electricity consumption
K | Uncertainties on the investment costs are highly dependent on the expected share of hot tap water demand covered by the heat pump

## 207.2 Air to air new
| Technology | Heat pump, Air-to-air, new one family house
| Energy/technical data | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
[6 empty] | Lower | Upper | Lower | Upper
| Heat production capacity for one unit (kW) | 2.5 | 2.5 | 3.5 | 3.5 | 2 | 5 | 2 | 5 |  | 1,2,5
| Electricity generation capacity for one unit (kW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Expected share of space heating demand covered by unit (%) | 60 | 60 | 60 | 60 | 50 | 70 | 40 | 80 | F | 1,2,7
| Expected share of hot tap water demand covered by unit (%) | 0 | 0 | 100 | 100 | 0 | 100 | 0 | 100 | F | 1.2
| Heat efficiency, annual average, net (%) | 480 | 490 | 340 | 360 | 330 | 510 | 330 | 520 | C, G, H, I | 4,5,7,8
| Total efficiency, annual average, net (%) | 480 | 490 | 340 | 360 | 330 | 510 | 330 | 520 | C, G, H, J | 4,5,7,8
| Auxiliary Electricity consumption (kWh/year) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Technical lifetime (years) | 12 | 12 | 12 | 12 | 10 | 15 | 10 | 15
Regulation ability
| Change in capacity within 1 minute (%) | 100 | 100 | 100 | 100 | 50 | 100 | 50 | 100 |  | 1,2,7
| Warm start-up time (hours) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1,2,7
| Cold start-up time (hours) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1,2,7
Environment
| SO2 (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| NOX (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| CH4 (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| N2O (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Particles (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Financial data
| Specific investment (1000€/unit) | 1.2 | 1.1 | 1.8 | 1.7 | 0.8 | 2 | 0.8 | 2 | K | 1,2,3,14
| - hereof equipment (%) | 75 | 75 | 70 | 70 | 50 | 80 | 50 | 80 |  | 1,2,7
| - hereof installation (%) | 25 | 25 | 30 | 30 | 20 | 50 | 20 | 50 |  | 1,2,7
Possible additional specific investment (1000€/unit)
| Fixed O&M (€/unit/year) | 170 | 161.6683 | 146.2099 | 132.263 | 150 | 250 | 100 | 150
| Variable O&M (€/MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1,2,7
References:
1 | Danfoss, 2015, information provided at workshop
2 | Bosch, 2015 , information provided at workshop
3 | Market and Statistics Report, EHPA 2014
5 | Energistyrelsen, 2015, conversation
7 | Teknologisk Institut, 2015, conversation
8 | Godkendelse af tilskudsberettigede anlæg, måling, dataindsamling og formidling, Teknologisk Institut 2013
14 | Heat implementation scenarios until 2030, Ecofys 2013
Notes:
C | Weighted by seasonal heat demand of average climate zones according to EN14825 and domestic hot water production according to EN16147
F | The share of heating demand and hot tap water demand covered depends on how the heat pump is operated in the total heat energy system in the house.
G | The reason for lower COP values compared to air-to-air heat pumps in existing buildings, is lower efficiency due to the small capacity of these heat pumps
H | The reason for the drop in COP values in 2030 and 2050, is hot tap water production from 2030 and onwards
I | Heat efficiency values refers to the COP of the heat pump
J | Total efficiency values are including auxilliary electricity consumption
K | Uncertainties on the investment costs are highly dependent on the expected share of hot tap water demand covered by the heat pump

## 207.3 Air to water existing
| Technology | Heat pump, Air-to-water, existing one family house
| Energy/technical data | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
[6 empty] | Lower | Upper | Lower | Upper
| Heat production capacity for one unit (kW) | 10 | 10 | 10 | 10 | 5 | 15 | 5 | 15 |  | 1,2,5
| Electricity generation capacity for one unit (kW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Expected share of space heating demand covered by unit (%) | 100 | 100 | 100 | 100 | 70 | 100 | 70 | 100 | A, F | 1,2,7
| Expected share of hot tap water demand covered by unit (%) | 100 | 100 | 100 | 100 | 70 | 100 | 70 | 100 | A, F | 1.2
| Heat efficiency, annual average, net (%), floor heating | 400 | 410 | 430 | 450 | 380 | 450 | 380 | 500 | C, I | 4,5,7,8
| Total efficiency, annual average, net (%), floor heating | 390 | 400 | 420 | 440 | 370 | 440 | 370 | 490 | C, J | 4,5,7,8
| Heat efficiency, annual average, net (%), radiators | 330 | 340 | 360 | 380 | 310 | 370 | 310 | 400 | C, I | 4,5,7,8
| Total efficiency, annual average, net (%), radiators | 325 | 335 | 355 | 370 | 300 | 360 | 300 | 390 | C, J | 4,5,7,8
| Auxiliary Electricity consumption (kWh/year) | 100 | 100 | 100 | 100 | 80 | 120 | 80 | 120 | L | 4
| Technical lifetime (years) | 18 | 18 | 18 | 18 | 15 | 20 | 15 | 20
Regulation ability
| Change in capacity within 1 minute (%) | 100 | 100 | 100 | 100 | 50 | 100 | 50 | 100 |  | 1,2,7
| Warm start-up time (hours) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1,2,7
| Cold start-up time (hours) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1,2,7
Environment
| SO2 (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| NOX (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| CH4 (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| N2O (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Particles (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Financial data
| Specific investment (1000€/unit) | 10 | 9.4 | 8.5 | 7.6 | 8 | 12 | 6 | 12 |  | 1,2,3,14
| - hereof equipment (%) | 70 | 70 | 65 | 60 | 50 | 85 | 50 | 85 | B | 1,2,7
| - hereof installation (%) | 30 | 30 | 35 | 40 | 15 | 50 | 15 | 50 |  | 1,2,7
Possible additional specific investment (1000€/unit)
| Fixed O&M (€/unit/year) | 291 | 278.0322 | 255.1166 | 238.7351 | 256 | 328 | 188 | 295
| - of which is electricity costs (€/unit/year) | 6 | 7 | 10 | 17 | 6 | 8 | 13 | 20 | L
| - of which is other O&M costs (€/unit/year) | 285 | 271.0322 | 245.1166 | 221.7351 | 250 | 320 | 175 | 275
| Variable O&M (€/MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1,2,7
References:
1 | Danfoss, 2015, information provided at workshop
2 | Bosch, 2015 , information provided at workshop
3 | Market and Statistics Report, EHPA 2014
4 | Sparenergi.dk, 2015
5 | Energistyrelsen, 2015, conversation
7 | Teknologisk Institut, 2015, conversation
8 | Godkendelse af tilskudsberettigede anlæg, måling, dataindsamling og formidling, Teknologisk Institut 2013
14 | Heat implementation scenarios until 2030, Ecofys 2013
Notes:
A | In gas hybrid installations the heat pump will cover around 70 % of the total heat demand
B | Including domestic hot water storage tank and auxiliary equipment
C | Weighted by seasonal heat demand of average climate zones according to EN14825 and domestic hot water production according to EN16147
F | The share of heating demand and hot tap water demand covered depends on how the heat pump is operated in the total heat energy system in the house.
G | The reason for lower COP values compared to air-to-air heat pumps in existing buildings, is lower efficiency due to the small capacity of these heat pumps
I | Heat efficiency values refers to the COP of the heat pump
J | Total efficiency values are including auxilliary electricity consumption
L | The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2015: 64, 2020: 71, 2030: 102, 2050: 165. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.

## 207.4 Air to water new
| Technology | Heat pump, Air-to-water, new one family house
| Energy/technical data | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
[6 empty] | Lower | Upper | Lower | Upper
| Heat production capacity for one unit (kW) | 4 | 4 | 4 | 4 | 2.5 | 6 | 2.5 | 6 |  | 1,2,5
| Electricity generation capacity for one unit (kW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Expected share of space heating demand covered by unit (%) | 100 | 100 | 100 | 100 | 70 | 100 | 70 | 100 | A, F | 1,2,7
| Expected share of hot tap water demand covered by unit (%) | 100 | 100 | 100 | 100 | 70 | 100 | 70 | 100 | A, F | 1.2
| Heat efficiency, annual average, net (%), floor heating | 345 | 355 | 365 | 380 | 330 | 365 | 330 | 400 | C, I | 4,5,7,8
| Total efficiency, annual average, net (%), floor heating | 325 | 335 | 345 | 365 | 315 | 345 | 315 | 390 | C, J | 4,5,7,8
| Heat efficiency, annual average, net (%), radiators | 300 | 320 | 340 | 355 | 290 | 330 | 290 | 375 | C, I | 4,5,7,8
| Total efficiency, annual average, net (%), radiators | 285 | 305 | 320 | 335 | 280 | 315 | 280 | 365 | C, J | 4,5,7,8
| Auxiliary Electricity consumption (kWh/year) | 100 | 100 | 100 | 100 | 80 | 120 | 80 | 120 | L | 4
| Technical lifetime (years) | 18 | 18 | 18 | 18 | 15 | 20 | 15 | 20
Regulation ability
| Change in capacity within 1 minute (%) | 100 | 100 | 100 | 100 | 50 | 100 | 50 | 100 |  | 1,2,7
| Warm start-up time (hours) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1,2,7
| Cold start-up time (hours) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1,2,7
Environment
| SO2 (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| NOX (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| CH4 (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| N2O (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Particles (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Financial data
| Specific investment (1000€/unit) | 7 | 6.6 | 5.9 | 5.3 | 6 | 9 | 4 | 8 |  | 1,2,3,13,14
| - hereof equipment (%) | 60 | 60 | 50 | 50 | 45 | 85 | 40 | 85 | B | 1,2,7
| - hereof installation (%) | 40 | 40 | 50 | 50 | 15 | 55 | 15 | 60 |  | 1,2,7
Possible additional specific investment (1000€/unit)
| Fixed O&M (€/unit/year) | 291 | 278.0322 | 255.1166 | 238.7351 | 256 | 328 | 188 | 295
| - of which is electricity costs (€/unit/year) | 6 | 7 | 10 | 17 | 6 | 8 | 13 | 20 | L
| - of which is other O&M costs (€/unit/year) | 285 | 271.0322 | 245.1166 | 221.7351 | 250 | 320 | 175 | 275
| Variable O&M (€/MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1,2,7
References:
1 | Danfoss, 2015, information provided at workshop
2 | Bosch, 2015 , information provided at workshop
3 | Market and Statistics Report, EHPA 2014
4 | Sparenergi.dk, 2015
5 | Energistyrelsen, 2015, conversation
7 | Teknologisk Institut, 2015, conversation
8 | Godkendelse af tilskudsberettigede anlæg, måling, dataindsamling og formidling, Teknologisk Institut 2013
13 | Afdækning af potentiale for varmepumper til opvarmning af helårshuse i Danmark til erstatning for oliefyr, Energistyrelsen 2011
14 | Heat implementation scenarios until 2030, Ecofys 2013
Notes:
A | In gas hybrid installations the heat pump will cover around 70 % of the total heat demand
B | Including domestic hot water storage tank and auxiliary equipment
C | Weighted by seasonal heat demand of average climate zones according to EN14825 and domestic hot water production according to EN16147
F | The share of heating demand and hot tap water demand covered depends on how the heat pump is operated in the total heat energy system in the house.
I | Heat efficiency values refers to the COP of the heat pump
J | Total efficiency values are including auxilliary electricity consumption
L | The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2015: 64, 2020: 71, 2030: 102, 2050: 165. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.

## 207.5 Air to water Apartm. ex
| Technology | Heat pump, Air-to-water, existing apartments
| Energy/technical data | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
[6 empty] | Lower | Upper | Lower | Upper
| Heat production capacity for one unit (kW) | 400 | 400 | 400 | 400 | 300 | 500 | 300 | 500 |  | 5.6
| Electricity generation capacity for one unit (kW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Expected share of space heating demand covered by unit (%) | 100 | 100 | 100 | 100 | 70 | 100 | 70 | 100 | F
| Expected share of hot tap water demand covered by unit (%) | 100 | 100 | 100 | 100 | 70 | 100 | 70 | 100 | F
| Heat efficiency, annual average, net (%), floor heating | 430 | 440 | 450 | 480 | 430 | 460 | 440 | 500 | C, I | 11,12,15
| Total efficiency, annual average, net (%), floor heating | 410 | 420 | 430 | 460 | 410 | 450 | 420 | 480 | C, J | 4,11,12,15
| Heat efficiency, annual average, net (%), radiators | 380 | 390 | 400 | 415 | 380 | 420 | 390 | 450 | C, I | 11,12,15
| Total efficiency, annual average, net (%), radiators | 365 | 375 | 390 | 405 | 370 | 410 | 375 | 430 | C, J | 4,11,12,15
| Auxiliary Electricity consumption (kWh/year) | 10000 | 10000 | 10000 | 10000 | 8000 | 12000 | 8000 | 12000 | L | 4.7
| Technical lifetime (years) | 20 | 20 | 20 | 20 | 15 | 25 | 15 | 25 |  | 7.12
Regulation ability
| Change in capacity within 1 minute (%) | 50 | 50 | 50 | 50 | 10 | 100 | 10 | 100 |  | 7.11
| Warm start-up time (hours) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 11
| Cold start-up time (hours) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 11
Environment
| SO2 (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| NOX (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| CH4 (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| N2O (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Particles (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Financial data
| Specific investment (1000€/unit) | 150 | 141 | 127 | 114 | 130 | 160 | 100 | 150 |  | 12.15
| - hereof equipment (%) | 70 | 70 | 70 | 70 | 50 | 85 | 50 | 85 | B | 12
| - hereof installation (%) | 30 | 30 | 30 | 30 | 15 | 50 | 15 | 50 |  | 12
Possible additional specific investment (1000€/unit)
| Fixed O&M (€/unit/year) | 1640 | 1650 | 1866 | 2411 | 1070 | 2850 | 1820 | 3980
| - of which is electricity costs (€/unit/year) | 640 | 710 | 1020 | 1650 | 570 | 850 | 1320 | 1980 | L
| - of which is other O&M costs (€/unit/year) | 1000 | 940 | 846 | 761 | 500 | 2000 | 500 | 2000 |  | 12
| Variable O&M (€/MWh) | 0.5 | 0.47 | 0.42 | 0.38 | 0.2 | 1 | 0.2 | 1 |  | 12
References:
4 | Sparenergi.dk, 2015
5 | Energistyrelsen, 2015, conversation
6 | Energinet.dk, 2015, conversation
7 | Teknologisk Institut, 2015, conversation
11 | Cronborg, 2015, conversation
12 | Drejebog til store varmepumpeprojekter i fjernvarmesystemet, Energistyrelsen 2015
15 | Udredning vedrørende varmelagringsteknologier og store varmepumper til brug i fjernvarmesystemer, Energistyrelsen 2013
Notes:
B | Including domestic hot water storage tank and auxiliary equipment
C | Weighted by seasonal heat demand of average climate zones according to EN14825 and domestic hot water production according to EN16147
F | The share of heating demand and hot tap water demand covered depends on how the heat pump is operated in the total heat energy system in the house.
I | Heat efficiency values refers to the COP of the heat pump
J | Total efficiency values are including auxilliary electricity consumption
L | The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2015: 64, 2020: 71, 2030: 102, 2050: 165. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.

## 207.6 Air to water Apartm. new
| Technology | Heat pump, Air-to-water, new apartments
| Energy/technical data | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
[6 empty] | Lower | Upper | Lower | Upper
| Heat production capacity for one unit (kW) | 160 | 160 | 160 | 160 | 140 | 200 | 140 | 200 |  | 5.6
| Electricity generation capacity for one unit (kW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Expected share of space heating demand covered by unit (%) | 100 | 100 | 100 | 100 | 70 | 100 | 70 | 100 | F
| Expected share of hot tap water demand covered by unit (%) | 100 | 100 | 100 | 100 | 70 | 100 | 70 | 100 | F
| Heat efficiency, annual average, net (%), floor heating | 440 | 450 | 460 | 480 | 440 | 470 | 450 | 520 | C, I | 11,12,15
| Total efficiency, annual average, net (%), floor heating | 390 | 400 | 405 | 410 | 390 | 410 | 400 | 490 | C, J | 4,11,12,15
| Heat efficiency, annual average, net (%), radiators | 420 | 430 | 440 | 460 | 420 | 460 | 430 | 500 | C, I | 11,12,15
| Total efficiency, annual average, net (%), radiators | 370 | 380 | 390 | 405 | 370 | 400 | 380 | 480 | C, J | 4,11,12,15
| Auxiliary Electricity consumption (kWh/year) | 10000 | 10000 | 10000 | 10000 | 8000 | 12000 | 8000 | 12000 | L | 4.7
| Technical lifetime (years) | 20 | 20 | 20 | 20 | 15 | 25 | 15 | 25 |  | 7.12
Regulation ability
| Change in capacity within 1 minute (%) | 100 | 100 | 100 | 100 | 20 | 100 | 20 | 100 |  | 7.11
| Warm start-up time (hours) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7.11
| Cold start-up time (hours) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7.11
Environment
| SO2 (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| NOX (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| CH4 (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| N2O (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Particles (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Financial data
| Specific investment (1000€/unit) | 75 | 71 | 63 | 57 | 60 | 100 | 50 | 100 |  | 12.15
| - hereof equipment (%) | 60 | 60 | 60 | 60 | 50 | 85 | 50 | 85 | B | 12
| - hereof installation (%) | 40 | 40 | 40 | 40 | 15 | 50 | 15 | 50 |  | 12
Possible additional specific investment (1000€/unit)
| Fixed O&M (€/unit/year) | 1640 | 1650 | 1866 | 2411 | 1070 | 2850 | 1820 | 3980
| - of which is electricity costs (€/unit/year) | 640 | 710 | 1020 | 1650 | 570 | 850 | 1320 | 1980 | L
| - of which is other O&M costs (€/unit/year) | 1000 | 940 | 846 | 761 | 500 | 2000 | 500 | 2000 |  | 12
| Variable O&M (€/MWh) | 0.5 | 0.47 | 0.42 | 0.38 | 0.2 | 1 | 0.2 | 1 |  | 12
References:
4 | Sparenergi.dk, 2015
5 | Energistyrelsen, 2015, conversation
6 | Energinet.dk, 2015, conversation
7 | Teknologisk Institut, 2015, conversation
11 | Cronborg, 2015, conversation
12 | Drejebog til store varmepumpeprojekter i fjernvarmesystemet, Energistyrelsen 2015
15 | Udredning vedrørende varmelagringsteknologier og store varmepumper til brug i fjernvarmesystemer, Energistyrelsen 2013
Notes:
B | Including domestic hot water storage tank and auxiliary equipment
C | Weighted by seasonal heat demand of average climate zones according to EN14825 and domestic hot water production according to EN16147
F | The share of heating demand and hot tap water demand covered depends on how the heat pump is operated in the total heat energy system in the house.
I | Heat efficiency values refers to the COP of the heat pump
J | Total efficiency values are including auxilliary electricity consumption
L | The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2015: 64, 2020: 71, 2030: 102, 2050: 165. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.

## 207.7 Ground source existing
| Technology | Heat pump, ground source, existing one family house
| Energy/technical data | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
[6 empty] | Lower | Upper | Lower | Upper
| Heat production capacity for one unit (kW) | 10 | 10 | 10 | 10 | 5 | 15 | 5 | 15 |  | 1,2,5
| Electricity generation capacity for one unit (kW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Expected share of space heating demand covered by unit (%) | 100 | 100 | 100 | 100 | 80 | 100 | 80 | 100 | F | 1,2,7
| Expected share of hot tap water demand covered by unit (%) | 100 | 100 | 100 | 100 | 80 | 100 | 80 | 100 | F | 1.2
| Heat efficiency, annual average, net (%), floor heating | 440 | 450 | 460 | 485 | 420 | 480 | 420 | 500 | C, I | 4,5,7,8
| Total efficiency, annual average, net (%), floor heating | 430 | 440 | 450 | 475 | 410 | 460 | 410 | 480 | C, J | 4,5,7,8
| Heat efficiency, annual average, net (%), radiators | 370 | 380 | 390 | 405 | 360 | 400 | 360 | 420 | C, I | 4,5,7,8
| Total efficiency, annual average, net (%), radiators | 360 | 370 | 380 | 395 | 350 | 380 | 350 | 405 | C, J | 4,5,7,8
| Auxiliary Electricity consumption (kWh/year) | 100 | 100 | 100 | 100 | 80 | 120 | 80 | 120 | L | 4
| Technical lifetime (years) | 20 | 20 | 20 | 20 | 15 | 25 | 15 | 25 |  | 1,2,7
Regulation ability
| Change in capacity within 1 minute (%) | 100 | 100 | 100 | 100 | 50 | 100 | 50 | 100 |  | 1,2,7
| Warm start-up time (hours) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1,2,7
| Cold start-up time (hours) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1,2,7
Environment
| SO2 (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| NOX (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| CH4 (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| N2O (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Particles (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Financial data
| Specific investment (1000€/unit) | 16 | 15 | 14 | 12 | 13 | 17 | 10 | 16 | D | 1,2,3,14
| - hereof equipment (%) | 65 | 65 | 65 | 65 | 55 | 75 | 55 | 85 | B | 1,2,7
| - hereof installation (%) | 35 | 35 | 35 | 35 | 25 | 45 | 15 | 45 |  | 1,2,7
Possible additional specific investment (1000€/unit)
| Fixed O&M (€/unit/year) | 291 | 278.0322 | 255.1166 | 238.7351 | 256 | 328 | 188 | 295
| - of which is electricity costs (€/unit/year) | 6 | 7 | 10 | 17 | 6 | 8 | 13 | 20 | L
| - of which is other O&M costs (€/unit/year) | 285 | 271.0322 | 245.1166 | 221.7351 | 250 | 320 | 175 | 275
| Variable O&M (€/MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1,2,7
References:
1 | Danfoss, 2015, information provided at workshop
2 | Bosch, 2015 , information provided at workshop
3 | Market and Statistics Report, EHPA 2014
4 | Sparenergi.dk, 2015
5 | Energistyrelsen, 2015, conversation
7 | Teknologisk Institut, 2015, conversation
8 | Godkendelse af tilskudsberettigede anlæg, måling, dataindsamling og formidling, Teknologisk Institut 2013
14 | Heat implementation scenarios until 2030, Ecofys 2013
Notes:
B | Including domestic hot water storage tank and auxiliary equipment
C | Weighted by seasonal heat demand of average climate zones according to EN14825 and domestic hot water production according to EN16147
D | The replacement cost of a worn out ground source heat pump will usually only be around 30 % of the initial investment as some components are reused
F | The share of heating demand and hot tap water demand covered depends on how the heat pump is operated in the total heat energy system in the house.
I | Heat efficiency values refers to the COP of the heat pump
J | Total efficiency values are including auxilliary electricity consumption
L | The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2015: 64, 2020: 71, 2030: 102, 2050: 165. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.

## 207.8 Ground source new
| Technology | Heat pump, ground source, new one family house
| Energy/technical data | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
[6 empty] | Lower | Upper | Lower | Upper
| Heat production capacity for one unit (kW) | 4 | 4 | 4 | 4 | 2.5 | 6 | 2.5 | 6 |  | 1,2,5
| Electricity generation capacity for one unit (kW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Expected share of space heating demand covered by unit (%) | 100 | 100 | 100 | 100 | 80 | 100 | 80 | 100 | F | 1,2,7
| Expected share of hot tap water demand covered by unit (%) | 100 | 100 | 100 | 100 | 80 | 100 | 80 | 100 | F | 1.2
| Heat efficiency, annual average, net (%), floor heating | 355 | 365 | 375 | 390 | 335 | 385 | 335 | 410 | C, I | 4,5,7,8
| Total efficiency, annual average, net (%), floor heating | 335 | 345 | 360 | 375 | 325 | 375 | 325 | 400 | C, J | 4,5,7,8
| Heat efficiency, annual average, net (%), radiators | 310 | 320 | 330 | 345 | 300 | 340 | 300 | 380 | C, I | 4,5,7,8
| Total efficiency, annual average, net (%), radiators | 295 | 305 | 315 | 330 | 285 | 325 | 285 | 370 | C, J | 4,5,7,8
| Auxiliary Electricity consumption (kWh/year) | 100 | 100 | 100 | 100 | 80 | 120 | 80 | 120 | L | 4
| Technical lifetime (years) | 20 | 20 | 20 | 20 | 15 | 25 | 15 | 25 |  | 1,2,7
Regulation ability
| Change in capacity within 1 minute (%) | 100 | 100 | 100 | 100 | 50 | 100 | 50 | 100 |  | 1,2,7
| Warm start-up time (hours) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1,2,7
| Cold start-up time (hours) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1,2,7
Environment
| SO2 (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| NOX (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| CH4 (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| N2O (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Particles (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Financial data
| Specific investment (1000€/unit) | 12 | 11 | 10 | 9 | 9 | 13 | 8 | 14 | D | 1,2,3,13,14
| - hereof equipment (%) | 55 | 55 | 55 | 55 | 45 | 65 | 45 | 75 | B | 1,2,7
| - hereof installation (%) | 45 | 45 | 45 | 45 | 35 | 55 | 25 | 55 |  | 1,2,7
Possible additional specific investment (1000€/unit)
| Fixed O&M (€/unit/year) | 291 | 278.0322 | 255.1166 | 238.7351 | 256 | 328 | 188 | 295
| - of which is electricity costs (€/unit/year) | 6 | 7 | 10 | 17 | 6 | 8 | 13 | 20 | L
| - of which is other O&M costs (€/unit/year) | 285 | 271.0322 | 245.1166 | 221.7351 | 250 | 320 | 175 | 275
| Variable O&M (€/MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1,2,7
References:
1 | Danfoss, 2015, information provided at workshop
2 | Bosch, 2015 , information provided at workshop
3 | Market and Statistics Report, EHPA 2014
4 | Sparenergi.dk, 2015
5 | Energistyrelsen, 2015, conversation
7 | Teknologisk Institut, 2015, conversation
8 | Godkendelse af tilskudsberettigede anlæg, måling, dataindsamling og formidling, Teknologisk Institut 2013
14 | Heat implementation scenarios until 2030, Ecofys 2013
Notes:
B | Including domestic hot water storage tank and auxiliary equipment
C | Weighted by seasonal heat demand of average climate zones according to EN14825 and domestic hot water production according to EN16147
D | The replacement cost of a worn out ground source heat pump will usually only be around 30 % of the initial investment as some components are reused
F | The share of heating demand and hot tap water demand covered depends on how the heat pump is operated in the total heat energy system in the house.
I | Heat efficiency values refers to the COP of the heat pump
J | Total efficiency values are including auxilliary electricity consumption
L | The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2015: 64, 2020: 71, 2030: 102, 2050: 165. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.

## 207.9 Ground apartm. exis
| Technology | Heat pump, Ground source, existing apartments
| Energy/technical data | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
[6 empty] | Lower | Upper | Lower | Upper
| Heat production capacity for one unit (kW) | 400 | 400 | 400 | 400 | 300 | 500 | 300 | 500 |  | 5.6
| Electricity generation capacity for one unit (kW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Expected share of space heating demand covered by unit (%) | 100 | 100 | 100 | 100 | 70 | 100 | 70 | 100 | F
| Expected share of hot tap water demand covered by unit (%) | 100 | 100 | 100 | 100 | 70 | 100 | 70 | 100 | F
| Heat efficiency, annual average, net (%), floor heating | 470 | 480 | 490 | 510 | 470 | 500 | 470 | 550 | C, I | 11,12,15
| Total efficiency, annual average, net (%), floor heating | 450 | 460 | 470 | 490 | 450 | 480 | 450 | 530 | C, J | 4,11,12,15
| Heat efficiency, annual average, net (%), radiators | 420 | 430 | 440 | 460 | 420 | 450 | 420 | 500 | C, I | 11,12,15
| Total efficiency, annual average, net (%), radiators | 400 | 410 | 420 | 440 | 400 | 430 | 400 | 480 | C, J | 4,11,12,15
| Auxiliary Electricity consumption (kWh/year) | 10000 | 10000 | 10000 | 10000 | 8000 | 12000 | 8000 | 12000 | L | 4.7
| Technical lifetime (years) | 20 | 20 | 20 | 20 | 15 | 25 | 15 | 25 |  | 7.12
Regulation ability
| Change in capacity within 1 minute (%) | 50 | 50 | 50 | 50 | 10 | 100 | 10 | 100 |  | 7.11
| Warm start-up time (hours) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7.11
| Cold start-up time (hours) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7.11
Environment
| SO2 (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| NOX (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| CH4 (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| N2O (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Particles (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Financial data
| Specific investment (1000€/unit) | 265 | 249 | 224 | 202 | 235 | 265 | 200 | 265 |  | 12,13,15
| - hereof equipment (%) | 60 | 60 | 60 | 60 | 50 | 85 | 50 | 85 | B | 12.13
| - hereof installation (%) | 40 | 40 | 40 | 40 | 15 | 50 | 15 | 50 |  | 12.13
Possible additional specific investment (1000€/unit)
| Fixed O&M (€/unit/year) | 1640 | 1650 | 1866 | 2411 | 1070 | 2850 | 1820 | 3980
| - of which is electricity costs (€/unit/year) | 640 | 710 | 1020 | 1650 | 570 | 850 | 1320 | 1980 | L
| - of which is other O&M costs (€/unit/year) | 1000 | 940 | 846 | 761 | 500 | 2000 | 500 | 2000 |  | 12
| Variable O&M (€/MWh) | 0.5 | 0.47 | 0.42 | 0.38 | 0.2 | 1 | 0.2 | 1 |  | 12
References:
4 | Sparenergi.dk, 2015
5 | Energistyrelsen, 2015, conversation
6 | Energinet.dk, 2015, conversation
7 | Teknologisk Institut, 2015, conversation
11 | Cronborg, 2015, conversation
12 | Drejebog til store varmepumpeprojekter i fjernvarmesystemet, Energistyrelsen 2015
13 | Afdækning af potentiale for varmepumper til opvarmning af helårshuse i Danmark til erstatning for oliefyr, Energistyrelsen 2011
15 | Udredning vedrørende varmelagringsteknologier og store varmepumper til brug i fjernvarmesystemer, Energistyrelsen 2013
Notes:
B | Including domestic hot water storage tank and auxiliary equipment
C | Weighted by seasonal heat demand of average climate zones according to EN14825 and domestic hot water production according to EN16147
F | The share of heating demand and hot tap water demand covered depends on how the heat pump is operated in the total heat energy system in the house.
I | Heat efficiency values refers to the COP of the heat pump
J | Total efficiency values are including auxilliary electricity consumption
L | The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2015: 64, 2020: 71, 2030: 102, 2050: 165. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.

## 207.10 Ground apartm. new
| Technology | Heat pump, Ground source, new apartments
| Energy/technical data | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
[6 empty] | Lower | Upper | Lower | Upper
| Heat production capacity for one unit (kW) | 160 | 160 | 160 | 160 | 140 | 200 | 140 | 200 |  | 5.6
| Electricity generation capacity for one unit (kW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Expected share of space heating demand covered by unit (%) | 100 | 100 | 100 | 100 | 70 | 100 | 70 | 100 | F
| Expected share of hot tap water demand covered by unit (%) | 100 | 100 | 100 | 100 | 70 | 100 | 70 | 100 | F
| Heat efficiency, annual average, net (%), floor heating | 500 | 510 | 520 | 540 | 500 | 530 | 500 | 580 | C, I | 11,12,15
| Total efficiency, annual average, net (%), floor heating | 430 | 440 | 450 | 460 | 430 | 490 | 430 | 530 | C, J | 4,11,12,15
| Heat efficiency, annual average, net (%), radiators | 480 | 490 | 500 | 520 | 480 | 510 | 480 | 560 | C, I | 11,12,15
| Total efficiency, annual average, net (%), radiators | 420 | 430 | 440 | 455 | 420 | 470 | 420 | 520 | C, J | 4,11,12,15
| Auxiliary Electricity consumption (kWh/year) | 10000 | 10000 | 10000 | 10000 | 8000 | 12000 | 8000 | 12000 | L | 4.7
| Technical lifetime (years) | 20 | 20 | 20 | 20 | 15 | 25 | 15 | 25 |  | 7.12
Regulation ability
| Change in capacity within 1 minute (%) | 100 | 100 | 100 | 100 | 20 | 100 | 20 | 100 |  | 7.11
| Warm start-up time (hours) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7.11
| Cold start-up time (hours) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7.11
Environment
| SO2 (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| NOX (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| CH4 (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| N2O (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Particles (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Financial data
| Specific investment (1000€/unit) | 95 | 89 | 80 | 72 | 80 | 100 | 60 | 100 |  | 12,13,15
| - hereof equipment (%) | 50 | 50 | 50 | 50 | 40 | 80 | 40 | 80 | B | 12.13
| - hereof installation (%) | 50 | 50 | 50 | 50 | 20 | 60 | 20 | 60 |  | 12.13
Possible additional specific investment (1000€/unit)
| Fixed O&M (€/unit/year) | 1640 | 1650 | 1866 | 2411 | 1070 | 2850 | 1820 | 3980
| - of which is electricity costs (€/unit/year) | 640 | 710 | 1020 | 1650 | 570 | 850 | 1320 | 1980 | L
| - of which is other O&M costs (€/unit/year) | 1000 | 940 | 846 | 761 | 500 | 2000 | 500 | 2000 |  | 12
| Variable O&M (€/MWh) | 0.5 | 0.47 | 0.42 | 0.38 | 0.2 | 1 | 0.2 | 1 |  | 12
References:
4 | Sparenergi.dk, 2015
5 | Energistyrelsen, 2015, conversation
6 | Energinet.dk, 2015, conversation
7 | Teknologisk Institut, 2015, conversation
11 | Cronborg, 2015, conversation
12 | Drejebog til store varmepumpeprojekter i fjernvarmesystemet, Energistyrelsen 2015
13 | Afdækning af potentiale for varmepumper til opvarmning af helårshuse i Danmark til erstatning for oliefyr, Energistyrelsen 2011
15 | Udredning vedrørende varmelagringsteknologier og store varmepumper til brug i fjernvarmesystemer, Energistyrelsen 2013
Notes:
B | Including domestic hot water storage tank and auxiliary equipment
C | Weighted by seasonal heat demand of average climate zones according to EN14825 and domestic hot water production according to EN16147
F | The share of heating demand and hot tap water demand covered depends on how the heat pump is operated in the total heat energy system in the house.
I | Heat efficiency values refers to the COP of the heat pump
J | Total efficiency values are including auxilliary electricity consumption
L | The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2015: 64, 2020: 71, 2030: 102, 2050: 165. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.

## 207.11 Ventilation
| Technology | Heat pump, ventilation, new one family house
| Energy/technical data | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
[6 empty] | Lower | Upper | Lower | Upper
| Heat production capacity for one unit (kW) | 2 | 2 | 3 | 3 | 2 | 3 | 2 | 3 |  | 1,2,5
| Electricity generation capacity for one unit (kW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Expected share of space heating demand covered by unit (%) | 70 | 80 | 85 | 100 | 40 | 100 | 40 | 100 | F | 1,2,7
| Expected share of hot tap water demand covered by unit (%) | 90 | 90 | 100 | 100 | 0 | 100 | 0 | 100 | F | 1.2
| Heat efficiency, annual average, net (%) | 320 | 330 | 350 | 370 | 320 | 350 | 320 | 400 | C, I | 1,2,7
| Total efficiency, annual average, net (%) | 315 | 325 | 345 | 365 | 315 | 345 | 315 | 395 | C, J | 1,2,7
| Auxiliary Electricity consumption (kWh/year) | 30 | 30 | 30 | 30 | 20 | 40 | 20 | 50 | L | 7
| Technical lifetime (years) | 15 | 15 | 15 | 15 | 10 | 20 | 10 | 20 |  | 1,2,7
Regulation ability
| Change in capacity within 1 minute (%) | 100 | 100 | 100 | 100 | 50 | 100 | 50 | 100 |  | 1,2,7
| Warm start-up time (hours) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1,2,7
| Cold start-up time (hours) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1,2,7
Environment
| SO2 (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| NOX (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| CH4 (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| N2O (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Particles (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Financial data
| Specific investment (1000€/unit) | 2 | 1.9 | 1.7 | 1.5 | 1.5 | 2 | 1 | 2 | B, E | 3,9,10,14
| - hereof equipment (%) | 90 | 90 | 90 | 90 | 80 | 90 | 80 | 90 |  | 1,2,7
| - hereof installation (%) | 10 | 10 | 10 | 10 | 10 | 20 | 10 | 20 |  | 1,2,7
Possible additional specific investment (1000€/unit)
| Fixed O&M (€/unit/year) | 202 | 190 | 172 | 157 | 151 | 253 | 153 | 258
| - of which is electricity costs (€/unit/year) | 2 | 2 | 3 | 5 | 1 | 3 | 3 | 8 | L
| - of which is other O&M costs (€/unit/year) | 200 | 188 | 169 | 152 | 150 | 250 | 150 | 250 |  | 1,2,7
| Variable O&M (€/MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1,2,7
References:
1 | Danfoss, 2015, information provided at workshop
2 | Bosch, 2015 , information provided at workshop
3 | Market and Statistics Report, EHPA 2014
5 | Energistyrelsen, 2015, conversation
7 | Teknologisk Institut, 2015, conversation
9 | Nilan, 2015, conversation
10 | Genvex, 2015, conversation
14 | Heat implementation scenarios until 2030, Ecofys 2013
Notes:
B | Including domestic hot water storage tank and auxiliary equipment
C | Weighted by seasonal heat demand of average climate zones according to EN14825 and domestic hot water production according to EN16147
E | Add on price compared to ventilation unit without heat pump, cost includes domestic hot water storage tank and auxiliary equipment
F | The share of heating demand and hot tap water demand covered depends on how the heat pump is operated in the total heat energy system in the house.
I | Heat efficiency values refers to the COP of the heat pump
J | Total efficiency values are including auxilliary electricity consumption
L | The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2015: 64, 2020: 71, 2030: 102, 2050: 165. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.

## 207.12 Ventilation apartm. new
| Technology | Heat pump, ventilation, new apartments
| Energy/technical data | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
[6 empty] | Lower | Upper | Lower | Upper
| Heat production capacity for one unit (kW) | 160 | 160 | 160 | 160 | 140 | 200 | 140 | 200 |  | 5.6
| Electricity generation capacity for one unit (kW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Expected share of space heating demand covered by unit (%) | 100 | 100 | 100 | 100 | 70 | 100 | 70 | 100 | F
| Expected share of hot tap water demand covered by unit (%) | 100 | 100 | 100 | 100 | 70 | 100 | 70 | 100 | F
| Heat efficiency, annual average, net (%) | 550 | 560 | 570 | 590 | 550 | 580 | 550 | 620 | C, I | 11,12,15
| Total efficiency, annual average, net (%) | 530 | 540 | 550 | 570 | 530 | 560 | 530 | 600 | C, J | 4,11,12,15
| Auxiliary Electricity consumption (kWh/year) | 3000 | 3000 | 3000 | 3000 | 2000 | 4000 | 2000 | 4000 | L | 4.7
| Technical lifetime (years) | 15 | 15 | 15 | 15 | 12 | 20 | 12 | 20 |  | 7.12
Regulation ability
| Change in capacity within 1 minute (%) | 100 | 100 | 100 | 100 | 20 | 100 | 20 | 100 |  | 7.11
| Warm start-up time (hours) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7.11
| Cold start-up time (hours) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7.11
Environment
| SO2 (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| NOX (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| CH4 (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| N2O (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Particles (g per GJ fuel) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Financial data
| Specific investment (1000€/unit) | 75 | 71 | 63 | 57 | 60 | 100 | 50 | 100 |  | 12.15
| - hereof equipment (%) | 70 | 70 | 70 | 70 | 50 | 85 | 50 | 85 | B | 12
| - hereof installation (%) | 30 | 30 | 30 | 30 | 15 | 50 | 15 | 50 |  | 12
Possible additional specific investment (1000€/unit)
| Fixed O&M (€/unit/year) | 1195 | 1150 | 1151 | 1256 | 640 | 2285 | 830 | 2660
| - of which is electricity costs (€/unit/year) | 195 | 210 | 305 | 495 | 140 | 285 | 330 | 660 | L
| - of which is other O&M costs (€/unit/year) | 1000 | 940 | 846 | 761 | 500 | 2000 | 500 | 2000 |  | 12
| Variable O&M (€/MWh) | 0.5 | 0.47 | 0.42 | 0.38 | 0.2 | 1 | 0.2 | 1 |  | 12
References:
4 | Sparenergi.dk, 2015
5 | Energistyrelsen, 2015, conversation
6 | Energinet.dk, 2015, conversation
7 | Teknologisk Institut, 2015, conversation
11 | Cronborg, 2015, conversation
12 | Drejebog til store varmepumpeprojekter i fjernvarmesystemet, Energistyrelsen 2015
15 | Udredning vedrørende varmelagringsteknologier og store varmepumper til brug i fjernvarmesystemer, Energistyrelsen 2013
Notes:
B | Including domestic hot water storage tank and auxiliary equipment
C | Weighted by seasonal heat demand of average climate zones according to EN14825 and domestic hot water production according to EN16147
F | The share of heating demand and hot tap water demand covered depends on how the heat pump is operated in the total heat energy system in the house.
I | Heat efficiency values refers to the COP of the heat pump
J | Total efficiency values are including auxilliary electricity consumption
L | The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2015: 64, 2020: 71, 2030: 102, 2050: 165. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.

## 208.1 Absorption HP exis
| Technology | Heat pump absorption gas driven, one family house, existing buildings
| Energy/technical data | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
[6 empty] | Lower | Upper | Lower | Upper
| Heat production capacity for one unit (kW) | 18 | 30 | 30 | 30 | 10 | 50 | 10 | 50 | J,K,M,N,Q
| Electricity generation capacity for one unit (kW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Expected share of space heating demand covered by unit (%) | 100 | 100 | 100 | 100 | - | - | - | -
| Expected share of hot tap water demand covered by unit (%) | 100 | 100 | 100 | 100 | - | - | - | -
| Heat efficiency, annual average, net (%) | - | - | - | - | - | - | - | -
| Total efficiency, annual average, net (%) | 135 | 145 | 170 | 170 | - | - | - | - | B | 2.16
| Auxiliary Electricity consumption (kWh/year) | - | - | - | - | - | - | - | -
| Technical lifetime (years) | 20 | 20 | 20 | 20 | - | - | - | - | D
Regulation ability
| Change in capacity within 1 minute (%) | - | - | - | - | - | - | - | -
| Warm start-up time (hours) | - | - | - | - | - | - | - | -
| Cold start-up time (hours) | - | - | - | - | - | - | - | -
Environment
| SO2 (g per GJ fuel) | - | - | - | - | - | - | - | -
| NOX (g per GJ fuel) | 15 | 10 | 5 | 5 | - | - | - | - |  | 14
| CH4 (g per GJ fuel) | 2 | 1 | 0.5 | 0.5 | - | - | - | - | L
| N2O (g per GJ fuel) | 0 | 0 | 0 | 0 | - | - | - | - | L
| Particles (g per GJ fuel) | 0 | 0 | 0 | 0 | - | - | - | - | L
Financial data - air-to-water
| Specific investment (1000€/unit) | 13 | 12.22 | 10.998 | 9.8982 | - | - | - | - | A,E
| - hereof equipment (%) | 77 | 75 | 70 | 70 | - | - | - | -
| - hereof installation (%) | 23 | 25 | 30 | 30 | - | - | - | -
| Possible additional specific investment (1000€/unit) | 2 | 2 | 2 | 2 | - | - | - | - | I
| Fixed O&M (€/unit/year) | 235 | 235 | 235 | 235 | - | - | - | - | C
| Variable O&M (€/MWh) | 0 | 0 | 0 | 0 | - | - | - | - | D
Financial data - Brine-to-water (ground-source)
| Specific investment (1000€/unit) | 15.6 | 14.7 | 13.2 | 11.9 | - | - | - | - | A,E,F,G;H,P
| - hereof equipment (%) | 64 | 61 | 55 | 55 | - | - | - | - | O
| - hereof installation (%) | 36 | 39 | 45 | 45 | - | - | - | - | O
| Possible additional specific investment (1000€/unit) | 6.4 | 6.4 | 6.4 | 6.4 | - | - | - | - | I, J
| Fixed O&M (€/unit/year) | 235 | 235 | 235 | 235 | - | - | - | - | C
| Variable O&M (€/MWh) | 0 | 0 | 0 | 0 | - | - | - | - | D
References:
2 | Gas Heat Pumps. Efficient heating and cooling with natural gas. GasTerra / Castel International Publishers. Groningen, The Netherlands. 2010
14 | Innovative Technologien zur energetischen Nutzung von Gas, Prognos AG, 2009
16 | M. Näslund, Residential gas-fired sorption heat pumps. Test and technology evaluation, DGC 2008
Notes:
A | The cost “Specific investment” is split as following: Appliance + Installation of appliance + Heat collectors brine (when relevant). The cost of appliance in 2015 is difficult to appreciate as the technology is not yet on the market. However, considering the cost of the same technology sold today to commercial users (see next table) it is fair to think that the cost of the appliance alone will be around 10.000€ to start with; the target price once the appliance is on the market would be about 7-9000 € decreasing with time as production increases.
B | The Efficiency of the domestic version of Robur is not yet public, but it is announced in the same range as for the larger version of the heat pump (see also comments given next table). Efficiency given here is estimates of annual efficiency based on the data from manufacturers corrected from field test experience and literature. Higher efficiency may be obtained by using low-temperature distribution system (floor heating). The improvement of efficiency foreseen is both due to better technologies and a better interaction between the appliance and the heating installation.
C | Same as for gas boilers [1]. The most recent information for boilers service contract is about 135 without VAT. A similar cost is expected to apply to gas heat pumps. Note however, that the service is not mandatory for all appliances
D | Supposed to be the same as for gas boilers [1].
E | Electrical heat pump (air/water) installation cost is about 2000 € (15% of 13.000 €) according to [1] (table 5.18), a gas boiler installation is about 2500 € [1]. We consider that a gas heat pump air-water installation will cost about 3000 € once installers have learned the technology specificity. Most of the installation is not very different from a boiler installation apart from the air inlet.
F | The authors consider that a gas heat pump brine-water installation will cost the same as the air-water version (3000 €). This cost doesn’t include the heat collection (see G).
G | For the brine version the cost of the heat collection (horizontal) is 4000€ for single-family houses according to source such as (http://www.renvarme.dk/produkter/jordvarme-boringer.aspx?language=da-dk). The data is conform to the figure given for EHP in [1] (based on a 10 kW (capacity) heat pump). The gas heat pumps require less heat collectors, the cost compared to the electrical counterpart will be lower. (40% [2] to 50% [3] of the drilling of the corresponding ground source EHPs; similar figures will also apply for horizontal pipes). The authors expect this to result in a heat collection cost that is about 20% lower. So it will be 3200 € for a 10 kW heat pump (the authors keep 10 kW for comparison purpose with EHP). The initial cost is given with VAT, so the final figure for a 10 kW gas heat pumps is 2600 €.
H | The above figure will need to be validated with market data once the technology is on the market.
I | Possible installation of a new gas service line grid connection= 1600 €; for new installation only
J | In case of vertical drilling for electric heat pumps; there is the “additional cost” of a vertical heat collector of 6000 Euros (hardware + labour) compared to the price of an horizontal heat collector. See [1] The authors have considered that corresponding costs for gas heat pumps would be 20% lower (so 4800 Euros)
K | Based on Robur prototype.
L | Same as for boiler (the burner is a premix burner as for gas boilers).
M | The present capacity will probably be extended in both ends of the range.
N | The appliance can modulate between two values of the capacity. Here, we give the maximum capacity.
O | For the % calculation; “equipment %” is the cost of the heat pump, and “installation %” is all other cost (labour cost for installation + labour and hardware for the heat collector installation).
P | 100% of the investment cost is here given per unit and thus not depending on kW (cost based on one appliance on the market; so it is not possible to make a linear cost model).
Q | The solution most commonly used to cover larger heat demand is to use several units in cascade when needed.

## 208.2 Absorption HP Apart
| Technology | Heat pump absorption gas driven, apartment complex, existing buildings
| Energy/technical data | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
[6 empty] | Lower | Upper | Lower | Upper
| Heat production capacity for one unit (kW) | 44 | 80 | 80 | 80 | - | - | - | - | J,N
| Electricity generation capacity for one unit (kW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Expected share of space heating demand covered by unit (%) | 100 | 100 | 100 | 100 | - | - | - | -
| Expected share of hot tap water demand covered by unit (%) | 100 | 100 | 100 | 100 | - | - | - | -
| Heat efficiency, annual average, net (%) | - | - | - | - | - | - | - | -
| Total efficiency, annual average, net (%) | 135 | 145 | 170 | 170 | - | - | - | - | B | 2.16
| Auxiliary Electricity consumption (kWh/year) | - | - | - | - | - | - | - | -
| Technical lifetime (years) | 20 | 20 | 20 | 20 | - | - | - | - | D
Regulation ability
| Change in capacity within 1 minute (%) | - | - | - | - | - | - | - | -
| Warm start-up time (hours) | - | - | - | - | - | - | - | -
| Cold start-up time (hours) | - | - | - | - | - | - | - | -
Environment
| SO2 (g per GJ fuel) | - | - | - | - | - | - | - | -
| NOX (g per GJ fuel) | 15 | 10 | 5 | 5 | - | - | - | - |  | 14
| CH4 (g per GJ fuel) | 2 | 1 | 0.5 | 0.5 | - | - | - | - | K
| N2O (g per GJ fuel) | 0 | 0 | 0 | 0 | - | - | - | - | K
| Particles (g per GJ fuel) | 0 | 0 | 0 | 0 | - | - | - | - | K
Financial data - air-to-water
| Specific investment (1000€/unit) | 18 | 17 | 15 | 14 | - | - | - | - | A,E
| - hereof equipment (%) | 78 | 78 | 78 | 78 | - | - | - | -
| - hereof installation (%) | 22 | 22 | 22 | 22 | - | - | - | -
| Possible additional specific investment (1000€/unit) | 1.6 | 1.6 | 1.6 | 1.6 | - | - | - | - | I
| Fixed O&M (€/unit/year) | 235 | 235 | 235 | 235 | - | - | - | - | C
| Variable O&M (€/MWh) | 0 | 0 | 0 | 0 | - | - | - | - | D
Financial data - Brine-to-water (ground-source)
| Specific investment (1000€/unit) | 33 | 31.02 | 27.918 | 25.1262 | - | - | - | - | A,E,F,H,M
| - hereof equipment (%) | 42 | 42 | 42 | 42 | - | - | - | - | L
| - hereof installation (%) | 58 | 58 | 58 | 58 | - | - | - | - | L
| Possible additional specific investment (1000€/unit) | 24.6 | 24.6 | 24.6 | 24.6 | - | - | - | - | G,I
| Fixed O&M (€/unit/year) | 235 | 235 | 235 | 235 | - | - | - | - | C
| Variable O&M (€/MWh) | 0 | 0 | 0 | 0 | - | - | - | - | D
References:
2 | Gas Heat Pumps. Efficient heating and cooling with natural gas. GasTerra / Castel International Publishers. Groningen, The Netherlands. 2010
14 | Innovative Technologien zur energetischen Nutzung von Gas, Prognos AG, 2009
16 | M. Näslund, Residential gas-fired sorption heat pumps. Test and technology evaluation, DGC 2008
Notes:
A | Costs are based on a 44 kW unit. The cost “Specific investment” is split as following: Appliance + Installation of appliance + Heat collectors brine (when relevant). The cost for the appliance alone in 2015 is stable as the technology is already present for a number of years. Maybe the price will decrease a bit thanks to the higher production numbers.
B | Efficiency given here is estimates of annual efficiency based on the data from manufacturers corrected from field test experience and literature. Higher efficiency can be obtained when using low-temperature distribution system (floor heating). The improvement of efficiency foreseen is both due to better technologies and a better interaction between the appliance and the heating installation. Test results available from [18] are claiming 142 to 149% annual efficiency.
C | Same as for gas boilers [1]. The most recent information for boilers service contract is about 135 without VAT. A similar cost is expected to apply to gas heat pumps. Note however, that the service is not mandatory for all appliances.
D | Supposed to be the same as for gas boilers [1].
E | Note that only very few appliances are installed in Denmark and the figures are, therefore, only rough approximates. The authors consider here that the installation of a single air-water gas heat pump will cost about 4000 € (same as for single-family house + 1000€) once installers have learned how to do the job. The installation of several units in cascade will be different, but there are no references in Denmark that allow us to make a correct assessment of this.
F | Same as E for the brine/water gas heat pump the authors believe that the installation cost of a single 44 kW appliance will be as for the air-water version (4000 €) And again, the installation of several units in cascade will be different, but there are no references in Denmark that allow us to make a correct assessment of this. This cost doesn’t include the heat collection (see G &H).
G | For the brine version the additional cost of the heat collection (vertical) is 670 €/kW for an apartment complex [1]. Because gas heat pumps require less heat collectors, the cost compared to the electrical counterpart will be lower. (40% [2] to 50% [3] of the drilling of the corresponding ground source EHPs was already mentioned. We expect this to result in a heat collection cost that is about 20% lower. So this figure will be 536 €/kW for an apartment complex. This will result in approx. 23.000 € for a 44 kW heat pump.
H | The cost of the horizontal heat collection for a 44 kW gas heat pump is not very clear to the authors (not much existing data) at the present time (and EHP data of [1] are not specific for larger installations. But, considering it is about 40% of a vertical collection in general for EHP, and that additional cost for vertical are given as below, we end up with a total cost for vertical of 38.000 Euro (=23/0,6). So the horizontal heat collection would be 15.000 Euros (38.000 -23.000) based on a 44 kW heat pump.
I | Possible installation of a new gas service line grid connection= 1600 €; for new installation only.
J | 2015 size is based on Robur information.
K | Same as for boiler (the burner is a premix burner as for gas boilers).
L | For the % calculation; “equipment %” is the cost of the heat pump, and “installation %“ is all other cost (labour cost for installation + labour and hardware for the heat collector installation).
M | 100% of the investment cost is here given per unit and thus not depending on kW (cost based on one appliance on the market; so it is not possible to make a linear cost model).
N | The appliance can modulate between two values of the capacity. Here, we give the maximum capacity.

## 208.3 Gas engine-driv Apart
| Technology | Heat pump gas-engine driven, apartment complex, existing buildings
|  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
| Heat production capacity for one unit (kW) | 50 | 50 | 50 | 50 | 20 | 80 | 20 | 80 | A,E,L | 5
| Electricity generation capacity for one unit (kW) | - | - | - | - | - | - | - | -
| Expected share of space heating demand covered by unit (%) | 100 | 100 | 100 | 100 | - | - | - | -
| Expected share of hot tap water demand covered by unit (%) | 100 | 100 | 100 | 100 | - | - | - | -
| Heat efficiency, annual average, net (%) | - | - | - | - | - | - | - | -
| Total efficiency, annual average, net (%) | 150 | 155 | 155 | 160 | - | - | - | - |  | 14
| Auxiliary Electricity consumption (kWh/year) | - | - | - | - | - | - | - | -
| Technical lifetime (years) | 15 | 20 | 20 | 20 | 15 | 20 | 15 | 20 | B
Regulation ability
| Change in capacity within 1 minute (%) | - | - | - | - | - | - | - | -
| Warm start-up time (hours) | - | - | - | - | - | - | - | -
| Cold start-up time (hours) | - | - | - | - | - | - | - | -
Environment
| SO2 (g per GJ fuel) | 0 | 0 | 0 | 0 | - | - | - | -
| NOX (g per GJ fuel) | 120 | 80 | 50 | 50 | 20 | 150 | 10 | 100 | C | 15
| CH4 (g per GJ fuel) | 5 | 5 | 5 | 5 | - | - | - | - | D
| N2O (g per GJ fuel) | - | - | - | - | - | - | - | -
| Particles (g per GJ fuel) | - | - | - | - | - | - | - | -
Financial data - air-to-water
| Specific investment (1000€/unit) | 4 | 4 | 3 | 3 | - | - | - | - | F,G,O
| - hereof equipment (%) | 83 | 83 | 83 | 83 | - | - | - | - | P
| - hereof installation (%) | 17 | 17 | 17 | 17 | - | - | - | - | P
| Possible additional specific investment (1000€/unit) | 1.6 | 1.6 | 1.6 | 1.6 | - | - | - | - | H,K
| Fixed O&M (€/unit/year) | 235 | 235 | 235 | 235 | - | - | - | - | I
| Variable O&M (€/MWh) | 0 | 0 | 0 | 0 | - | - | - | - | J
Financial data - Brine-to-water (ground-source)
| Specific investment (1000€/unit) | 19 | 17.86 | 16.074 | 14.4666 | - | - | - | - | F,G,O
| - hereof equipment (%) | 51 | 51 | 51 | 51 | - | - | - | - | P
| - hereof installation (%) | 49 | 49 | 49 | 49 | - | - | - | - | P
| Possible additional specific investment (1000€/unit) | 24.6 | 24.6 | 24.6 | 24.6 | - | - | - | - | H,K
| Fixed O&M (€/unit/year) | 235 | 235 | 235 | 235 | - | - | - | - | I
| Variable O&M (€/MWh) | 0 | 0 | 0 | 0 | - | - | - | - | J
References:
5 | Marktübersicht Gaswärmepumpen 2012, ASUE, www.asue.de
14 | Innovative Technologien zur energetischen Nutzung von Gas, Prognos AG, 2009
15 | NOx emissions of new technologies under ECOdesign LOT1. Note by Jean Schweitzer, DGC, December 2011. Draft2.
Notes:
A | Based on model by Aisin & Sanyo air-to-air & air-to-water technologies.
B | The authors consider that GHP has a similar lifetime as engine based mCHP, even though this may be conservative, as the technology has been on the market for many years and is mature. Lifetime should improve in the future.
C | Emission can be strongly reduced by using catalyst reduction technologies that may be a standard in products for larger appliances in the future.
D | The authors consider that CH4 emissions are in the same range as those for “MicroCHP gas engine”.
E | Although the 80 kW is not very suitable to single-family houses, the appliances are generally built as series of the same models of different power (here from 20 to 80 kW). Those last and larger appliances are of course more suitable to commercial buildings and multiple apartments heating.
F | Specific investment (1000€/unit) (installations) is given here as X+Y where X = installation of the appliances itself; and Y is the cost of the brine heat collectors (installation and hardware). For the costs of air/water heat pumps, the air exchanger is considered as part of the appliance. The authors consider here that the installation of a single air-water & brine -water gas heat pump will cost the same as absorption heat pumps. Here the costs are based on a 44kW unit.
G | The authors consider here that the horizontal heat collection for a 44 kW will cost the same as for absorption heat pumps. (15.000 Euros). Here the costs are based on a 44kW unit.
H | The authors consider here that the additional cost for the vertical heat collection will cost the same as for absorption heat pumps. (23.000 Euros). Here the costs are based on a 44kW unit.
I | Same as for gas boilers [1]. The most recent information for boilers service contract is about 135 without VAT. A similar cost is expected to apply to gas heat pumps. Note however, that the service is not mandatory for all appliances.
J | Supposed to be the same as for gas boilers [1].
K | Possible installation of a new gas service line grid connection= 1600 €; for new installation only.
L | The solution most commonly used to cover larger heat demand is to use the end range of technologies from the table (80 kW) and possibly use them in cascade when needed. Single appliances of over 80 kW exists, but are less common.
M | 0.5 (for 80 kW) and 1.4 (for 25 kW).
N | See also www.asue.de; www.berndt-enersys.de ; www.prognos.com
O | The values in % are given for the example of an appliance of 20,000 Euros
P | For the % calculation; “equipment %” is the cost of the heat pump, and “installation % “ is all other cost (labour cost for installation + labour and hardware for the heat collector installation).

## 208.4 Adsorp gas driv one fam
| Technology | Heat pump, adsorption gas driven, ground source, one family house, existing buildings
|  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
| Heat production capacity for one unit (kW) | 10 | 10 | 10 | 10 | 1.5 | 15 | 1.5 | 15 | F,G,H,I
| Electricity generation capacity for one unit (kW) | - | - | - | - | - | - | - | -
| Expected share of space heating demand covered by unit (%) | 100 | 100 | 100 | 100 | - | - | - | -
| Expected share of hot tap water demand covered by unit (%) | 100 | 100 | 100 | 100 | - | - | - | -
| Heat efficiency, annual average, net (%) | - | - | - | - | - | - | - | -
| Total efficiency, annual average, net (%) | 135 | 135 | 135 | 135 | - | - | - | - | B | 5.17
| Auxiliary Electricity consumption (kWh/year) | - | - | - | - | - | - | - | -
| Technical lifetime (years) | 20 | 20 | 20 | 20 | - | - | - | - | G
Regulation ability
| Change in capacity within 1 minute (%) | - | - | - | - | - | - | - | -
| Warm start-up time (hours) | - | - | - | - | - | - | - | -
| Cold start-up time (hours) | - | - | - | - | - | - | - | -
Environment
| SO2 (g per GJ fuel) | 0 | 0 | 0 | 0 | - | - | - | - | E
| NOX (g per GJ fuel) | 20 | 10 | 5 | 5 | - | - | - | - | E
| CH4 (g per GJ fuel) | 2 | 1 | 0.5 | 0.5 | - | - | - | - | E
| N2O (g per GJ fuel) | 0 | 0 | 0 | 0 | - | - | - | - | E
| Particles (g per GJ fuel) | 0 | 0 | 0 | 0 | - | - | - | - | E
Financial data
| Specific investment (1000€/unit) | 14 | 13.16 | 11.844 | 10.6596 | - | - | - | - | A,I,J
| - hereof equipment (%) | 71 | 71 | 71 | 71 | - | - | - | -
| - hereof installation (%) | 29 | 29 | 29 | 29 | - | - | - | -
| Possible additional specific investment (1000€/unit) | 1.6 | 1.6 | 1.6 | 1.6 | - | - | - | - | H
| Fixed O&M (€/unit/year) | 235 | 235 | 235 | 235 | - | - | - | - | C
| Variable O&M (€/MWh) | 0 | 0 | 0 | 0 | - | - | - | - | D
References:
5 | Marktübersicht Gaswärmepumpen 2012, ASUE, www.asue.de
17 | Gas heat pumps: product overview Engine driven heat pumps Thermally driven heat pumps Juliette PROMELLE, GDF SUEZ, Research division. GHP Workshop in Paris December 2011 GdfSuez
Notes:
A | Appliance cost = 10.000 Euros. Manufacturer data from www.glo24.eu, confirmed by E.ON Ruhrgas. The prices are, however, for the German market and include the appliance, a hot-water tank, the solar collectors and the system control. The authors consider that the installation cost will be similar to the other heat pumps technologies (4000 Euros).
B | The efficiency of 135 % is given for nominal conditions (by the manufacturer). More recent annual efficiency figure was found and is lower as expected. Test results available from [17] are claiming 113 to 122% annual efficiency (without solar) and 133 to 144% annual efficiency (with solar). It is not clear whether this is with or without hot water.
C | Same as for gas boilers [1]. The most recent information for boilers service contract is about 135 without VAT. A similar cost is expected to apply to gas heat pumps. Note however, that the service is not mandatory for all appliances.
D | Supposed to be the same as for gas boilers [1].
E | No test data available at this stage, but it is expected to be the same as boilers because the burner technology is the same as the one used for condensing boilers (fully premix).
F | The appliance we know today is targeting the domestic market and the range covered will probably increase to 40/50 kW for appliances dedicated to the commercial market.
G | There are no data available for the lifetime as the technology is very new. To be competitive with other technologies the targeted lifetime is to be about 20 years.
H | Possible installation of a new gas service line (grid connection= 1600 €); for new installation only.
I | Modulating appliance: between 1.5 and 15 kW.
J | 100% of the investment cost is here given per unit and thus not depending on kW (cost based on one appliance on the market; so it is not possible to make a linear cost model).

## 215 Solar heating
| Technology | Solar heating system - One-family house, existing building. | [9 empty] | Technology | Solar heating system - One-family house, Energy renovated. | [9 empty] | Technology | Solar heating system - One-family house, new building | [9 empty] | Technology | Solar heating system - Apartment complex, existing building | [9 empty] | Technology | Solar heating system - Apartment complex, new building
|  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref |  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref |  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref |  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref |  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper |  |  | Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper |  |  | Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper |  |  | Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper |  |  | Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
| Heat production capacity for one unit (kW) | 4.2 | 4.2 | 4.2 | 4.2 | 3 | 6 | 3 | 6 | A, I | 1 | Heat production capacity for one unit (kW) | 4.2 | 4.2 | 4.2 | 4.2 | 3 | 6 | 3 | 6 | A, I | 1 | Heat production capacity for one unit (kW) | 4.2 | 4.2 | 4.2 | 4.2 | 3 | 6 | 3 | 6 | A, I | 1 | Heat production capacity for one unit (kW) | 140 | 140 | 140 | 140 | 100 | 200 | 100 | 200 | A, I | 1 | Heat production capacity for one unit (kW) | 140 | 140 | 140 | 140 | 100 | 200 | 100 | 200 | A, I | 1
| Electricity generation capacity for one unit (kW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Electricity generation capacity for one unit (kW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Electricity generation capacity for one unit (kW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Electricity generation capacity for one unit (kW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Electricity generation capacity for one unit (kW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Expected share of space heating demand covered by unit (%) | 5 | 5 | 5 | 5 | 0 | 10 | 0 | 10 | B, I | 1 | Expected share of space heating demand covered by unit (%) | 10 | 10 | 10 | 10 | 0 | 15 | 0 | 15 | B, I | 1 | Expected share of space heating demand covered by unit (%) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | B, I | 1 | Expected share of space heating demand covered by unit (%) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | B, I | 1 | Expected share of space heating demand covered by unit (%) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | B, I | 1
| Expected share of hot tap water demand covered by unit (%) | 65 | 65 | 65 | 65 | 40 | 70 | 40 | 70 | B, I | 1 | Expected share of hot tap water demand covered by unit (%) | 65 | 65 | 65 | 65 | 40 | 70 | 40 | 70 | B, I | 1 | Expected share of hot tap water demand covered by unit (%) | 65 | 65 | 65 | 65 | 40 | 70 | 40 | 70 | B, I | 1 | Expected share of hot tap water demand covered by unit (%) | 65 | 65 | 65 | 65 | 40 | 70 | 40 | 70 | B, I | 1 | Expected share of hot tap water demand covered by unit (%) | 65 | 65 | 65 | 65 | 40 | 70 | 40 | 70 | B, I | 1
| Electric efficiency, annual average, net (%) | NA | NA | NA | NA | NA | NA | NA | NA |  |  | Electric efficiency, annual average, net (%) | NA | NA | NA | NA | NA | NA | NA | NA |  |  | Electric efficiency, annual average, net (%) | NA | NA | NA | NA | NA | NA | NA | NA |  |  | Electric efficiency, annual average, net (%) | NA | NA | NA | NA | NA | NA | NA | NA |  |  | Electric efficiency, annual average, net (%) | NA | NA | NA | NA | NA | NA | NA | NA
| Heat efficiency, annual average, net (%) | NA | NA | NA | NA | NA | NA | NA | NA |  |  | Heat efficiency, annual average, net (%) | NA | NA | NA | NA | NA | NA | NA | NA |  |  | Heat efficiency, annual average, net (%) | NA | NA | NA | NA | NA | NA | NA | NA |  |  | Heat efficiency, annual average, net (%) | NA | NA | NA | NA | NA | NA | NA | NA |  |  | Heat efficiency, annual average, net (%) | NA | NA | NA | NA | NA | NA | NA | NA
| Total efficiency, annual average, net (%) | NA | NA | NA | NA | NA | NA | NA | NA |  |  | Total efficiency, annual average, net (%) | NA | NA | NA | NA | NA | NA | NA | NA |  |  | Total efficiency, annual average, net (%) | NA | NA | NA | NA | NA | NA | NA | NA |  |  | Total efficiency, annual average, net (%) | NA | NA | NA | NA | NA | NA | NA | NA |  |  | Total efficiency, annual average, net (%) | NA | NA | NA | NA | NA | NA | NA | NA
| Auxiliary Electricity consumption (kWh/year) | 150 | 140 | 130 | 110 | 100 | 200 | 75 | 150 |  |  | Auxiliary Electricity consumption (kWh/year) | 150 | 140 | 130 | 110 | 100 | 200 | 75 | 150 |  |  | Auxiliary Electricity consumption (kWh/year) | 150 | 140 | 130 | 110 | 100 | 200 | 75 | 150 |  |  | Auxiliary Electricity consumption (kWh/year) | 3000 | 2800 | 2500 | 2000 | 2000 | 4000 | 1500 | 3000 |  |  | Auxiliary Electricity consumption (kWh/year) | 3000 | 2800 | 2500 | 2000 | 2000 | 4000 | 1500 | 3000
| Technical lifetime (years) | 20 | 25 | 30 | 30 | 20 | 30 | 25 | 35 | C | 1 | Technical lifetime (years) | 20 | 25 | 30 | 30 | 20 | 30 | 25 | 35 | C | 1 | Technical lifetime (years) | 20 | 25 | 30 | 30 | 20 | 30 | 25 | 35 | C | 1 | Technical lifetime (years) | 20 | 25 | 30 | 30 | 20 | 30 | 25 | 35 | C | 1 | Technical lifetime (years) | 20 | 25 | 30 | 30 | 20 | 30 | 25 | 35 | C | 1
| Regulation ability | [10 empty] | Regulation ability | [10 empty] | Regulation ability | [10 empty] | Regulation ability | [10 empty] | Regulation ability
| Primary regulation (% per 30 seconds) | NA | NA | NA | NA | NA | NA | NA | NA |  |  | Primary regulation (% per 30 seconds) | NA | NA | NA | NA | NA | NA | NA | NA |  |  | Primary regulation (% per 30 seconds) | NA | NA | NA | NA | NA | NA | NA | NA |  |  | Primary regulation (% per 30 seconds) | NA | NA | NA | NA | NA | NA | NA | NA |  |  | Primary regulation (% per 30 seconds) | NA | NA | NA | NA | NA | NA | NA | NA
| Secondary regulation (% per minute) | NA | NA | NA | NA | NA | NA | NA | NA |  |  | Secondary regulation (% per minute) | NA | NA | NA | NA | NA | NA | NA | NA |  |  | Secondary regulation (% per minute) | NA | NA | NA | NA | NA | NA | NA | NA |  |  | Secondary regulation (% per minute) | NA | NA | NA | NA | NA | NA | NA | NA |  |  | Secondary regulation (% per minute) | NA | NA | NA | NA | NA | NA | NA | NA
| Minimum load (% of full load) | NA | NA | NA | NA | NA | NA | NA | NA |  |  | Minimum load (% of full load) | NA | NA | NA | NA | NA | NA | NA | NA |  |  | Minimum load (% of full load) | NA | NA | NA | NA | NA | NA | NA | NA |  |  | Minimum load (% of full load) | NA | NA | NA | NA | NA | NA | NA | NA |  |  | Minimum load (% of full load) | NA | NA | NA | NA | NA | NA | NA | NA
| Warm start-up time (hours) | NA | NA | NA | NA | NA | NA | NA | NA |  |  | Warm start-up time (hours) | NA | NA | NA | NA | NA | NA | NA | NA |  |  | Warm start-up time (hours) | NA | NA | NA | NA | NA | NA | NA | NA |  |  | Warm start-up time (hours) | NA | NA | NA | NA | NA | NA | NA | NA |  |  | Warm start-up time (hours) | NA | NA | NA | NA | NA | NA | NA | NA
| Cold start-up time (hours) | NA | NA | NA | NA | NA | NA | NA | NA |  |  | Cold start-up time (hours) | NA | NA | NA | NA | NA | NA | NA | NA |  |  | Cold start-up time (hours) | NA | NA | NA | NA | NA | NA | NA | NA |  |  | Cold start-up time (hours) | NA | NA | NA | NA | NA | NA | NA | NA |  |  | Cold start-up time (hours) | NA | NA | NA | NA | NA | NA | NA | NA
| Environment | [10 empty] | Environment | [10 empty] | Environment | [10 empty] | Environment | [10 empty] | Environment
| SO2 (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | SO2 (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | SO2 (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | SO2 (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | SO2 (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NOX (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | NOX (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | NOX (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | NOX (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | NOX (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CH4 (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | CH4 (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | CH4 (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | CH4 (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | CH4 (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| N2O (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | N2O (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | N2O (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | N2O (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | N2O (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Particles (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Particles (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Particles (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Particles (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Particles (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Financial data | [10 empty] | Financial data | [10 empty] | Financial data | [10 empty] | Financial data | [10 empty] | Financial data
| Specific investment (1000€/unit) | 4.0268 | 3.6242 | 3.3557 | 2.6846 | 3.2215 | 4.4295 | 2.1477 | 2.953 | D | 6 | Specific investment (1000€/unit) | 3.3557 | 3.3557 | 2.6846 | 2.4161 | 2.6846 | 3.6913 | 1.9329 | 2.6577 | D | 6 | Specific investment (1000€/unit) | 2.6846 | 2.4161 | 2.1477 | 1.8792 | 2.1477 | 2.953 | 1.5034 | 2.0671 | D | 6 | Specific investment (1000€/unit) | 85.906 | 80.5369 | 73.8255 | 67.1141 | 68.7248 | 94.4966 | 53.6913 | 73.8255 | D | 6 | Specific investment (1000€/unit) | 80.5369 | 73.8255 | 67.1141 | 60.4027 | 64.4295 | 88.5906 | 48.3221 | 66.443 | D | 6
| - hereof equipment (%) | 65 | 65 | 65 | 65 | 60 | 70 | 60 | 70 |  |  | - hereof equipment (%) | 65 | 65 | 65 | 65 | 60 | 70 | 60 | 70 |  |  | - hereof equipment (%) | 65 | 65 | 65 | 65 | 60 | 70 | 60 | 70 |  |  | - hereof equipment (%) | 65 | 65 | 65 | 65 | 60 | 70 | 60 | 70 |  |  | - hereof equipment (%) | 65 | 65 | 65 | 65 | 60 | 70 | 60 | 70
| - hereof installation (%) | 35 | 35 | 35 | 35 | 30 | 40 | 30 | 40 |  |  | - hereof installation (%) | 35 | 35 | 35 | 35 | 30 | 40 | 30 | 40 |  |  | - hereof installation (%) | 35 | 35 | 35 | 35 | 30 | 40 | 30 | 40 |  |  | - hereof installation (%) | 35 | 35 | 35 | 35 | 30 | 40 | 30 | 40 |  |  | - hereof installation (%) | 35 | 35 | 35 | 35 | 30 | 40 | 30 | 40
| Possible additional specific investment (1000€/unit) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Possible additional specific investment (1000€/unit) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Possible additional specific investment (1000€/unit) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Possible additional specific investment (1000€/unit) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Possible additional specific investment (1000€/unit) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fixed O&M (€/unit/year) | 69.45 | 68.1749 | 68.7841 | 63.2153 | 46.9 | 93.8 | 48.775 | 97.55 |  |  | Fixed O&M (€/unit/year) | 69.45 | 68.1749 | 68.7841 | 63.2153 | 46.9 | 93.8 | 38.775 | 87.55 |  |  | Fixed O&M (€/unit/year) | 69.45 | 68.1749 | 68.7841 | 63.2153 | 46.9 | 93.8 | 38.775 | 87.55 |  |  | Fixed O&M (€/unit/year) | 389 | 388.2498 | 437.5 | 404 | 268 | 536 | 255.5 | 551 |  |  | Fixed O&M (€/unit/year) | 389 | 388.2498 | 437.5 | 404 | 268 | 536 | 255.5 | 551
| - of which is electricity costs (€/unit/year) | 9.45 | 9.66 | 13.13 | 12.87 | 6.9 | 13.8 | 8.775 | 17.55 | F |  | - of which is electricity costs (€/unit/year) | 9.45 | 9.66 | 13.13 | 12.87 | 6.9 | 13.8 | 8.775 | 17.55 | F |  | - of which is electricity costs (€/unit/year) | 9.45 | 9.66 | 13.13 | 12.87 | 6.9 | 13.8 | 8.775 | 17.55 | F |  | - of which is electricity costs (€/unit/year) | 189 | 193.2 | 252.5 | 234 | 138 | 276 | 175.5 | 351 | F |  | - of which is electricity costs (€/unit/year) | 189 | 193.2 | 252.5 | 234 | 138 | 276 | 175.5 | 351 | F
| - of which is other O&M costs (€/unit/year) | 60 | 58.5149 | 55.6541 | 50.3453 | 40 | 80 | 40 | 80 | E, H |  | - of which is other O&M costs (€/unit/year) | 60 | 58.5149 | 55.6541 | 50.3453 | 40 | 80 | 30 | 70 | E, H |  | - of which is other O&M costs (€/unit/year) | 60 | 58.5149 | 55.6541 | 50.3453 | 40 | 80 | 30 | 70 | E, H |  | - of which is other O&M costs (€/unit/year) | 200 | 195.0498 | 185 | 170 | 130 | 260 | 80 | 200 | E, H |  | - of which is other O&M costs (€/unit/year) | 200 | 195.0498 | 185 | 170 | 130 | 260 | 80 | 200 | E, H
| Variable O&M (€/MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Variable O&M (€/MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Variable O&M (€/MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Variable O&M (€/MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Variable O&M (€/MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Technology specific data | [10 empty] | Technology specific data | [10 empty] | Technology specific data | [10 empty] | Technology specific data | [10 empty] | Technology specific data
| Solar collector area , m² | 6 | 6 | 6 | 6 | 4 | 9 | 4 | 9 | I | 1 | Solar collector area , m² | 6 | 6 | 6 | 6 | 4 | 9 | 4 | 9 | I | 1 | Solar collector area , m² | 6 | 6 | 6 | 6 | 4.2857 | 8.5714 | 4.2857 | 8.5714 | I | 1 | Solar collector area, m² | 200 | 200 | 200 | 200 | 140 | 290 | 140 | 290 | I | 1 | Solar collector area , m² | 200 | 200 | 200 | 200 | 140 | 290 | 140 | 290 | I | 1
| Performance, kWh pr. m² collector per year | 400 | 425 | 450 | 500 | 300 | 450 | 400 | 550 | J | 1 | Performance, kWh pr. m² collector per year | 400 | 425 | 450 | 500 | 300 | 450 | 400 | 550 | J | 1 | Performance, kWh pr. m² collector per year | 425 | 450 | 475 | 500 | 300 | 450 | 400 | 550 | J | 1 | Performance, kWh pr. m² collector per year | 400 | 425 | 450 | 500 | 300 | 450 | 400 | 550 | J | 1 | Performance, kWh pr. m² collector per year | 425 | 450 | 475 | 500 | 300 | 450 | 400 | 550 | J | 1
References:
1 | Solvarme faktablade, www.altomsolvarme.dk.
6 | Recommendation: Converting solar thermal collector area into installed capacity (m2 to kWth). Technical note, IEA SHC 2004.
Notes:
A | Fixed average size but increasing efficiency is assumed. Typical range is from 3-15 m2 in one-family houses. 1 m2 is equivalent with 0.7 kW.
B | Annual yield from 400 to 500 kWh/m2. Highest figures for new buildings. General improvements and better storage technology assumed.
C | Increase due to better materials/fluids.
D | Depends on existing heating system. Savings if tank should be changed anyway. For new/renovated buildings solar system costs are lower because it is being installed during renovation/construction.
E | Service checks, liquid etc., 60 EUR/year in average for small systems and 200 EUR/year for large systems.
F | Electricity for solar pump and control. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2015: 63, 2020: 69, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
G | Pollution associated with the small amount of electricity needed for operation is neglected.
H | Assuming a cost-reduction of 0.5 % p.a., which in turn is assumed equivalent to the typical improvement of mature technologies.
I | The size of the solar heating units are usually determined by the hot water demand so the full load hours are maximized. The size of the units will not be very dependent of the room heating demand.
J | In new buildings the unit along with the piping system can be optimised which will result in a more efficient system in new buildings compared with existing buildings.

## 216 Electric heating
| Technology | Electric heating - One-famely house, new building | [9 empty] | Technology | Electric heating - Apartment complex, new building
|  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref |  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper |  |  | Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
| Heat production capacity for one unit (kW) | 3 | 3 | 3 | 3 | 2 | 7 | 2 | 7 |  |  | Heat production capacity for one unit (kW) | 160 | 160 | 160 | 160 | 100 | 250 | 100 | 250 | B
| Electricity generation capacity for one unit (kW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Electricity generation capacity for one unit (kW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Expected share of space heating demand covered by unit (%) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  |  | Expected share of space heating demand covered by unit (%) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
| Expected share of hot tap water demand covered by unit (%) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  |  | Expected share of hot tap water demand covered by unit (%) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
| Electric efficiency, annual average, net (%) | NA | NA | NA | NA | NA | NA | NA | NA |  |  | Electric efficiency, annual average, net (%) | NA | NA | NA | NA | NA | NA | NA | NA
| Heat efficiency, annual average, net (%) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  |  | Heat efficiency, annual average, net (%) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
| Total efficiency, annual average, net (%) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | A |  | Total efficiency, annual average, net (%) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | A
| Auxiliary Electricity consumption (kWh/year) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Auxiliary Electricity consumption (kWh/year) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Technical lifetime (years) | 30 | 30 | 30 | 30 | 25 | 30 | 25 | 30 |  |  | Technical lifetime (years) | 30 | 30 | 30 | 30 | 25 | 30 | 25 | 30
| Regulation ability | [10 empty] | Regulation ability
| Primary regulation (% per 30 seconds) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  |  | Primary regulation (% per 30 seconds) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
| Secondary regulation (% per minute) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  |  | Secondary regulation (% per minute) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
| Minimum load (% of full load) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Minimum load (% of full load) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Warm start-up time (hours) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Warm start-up time (hours) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cold start-up time (hours) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Cold start-up time (hours) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Environment | [10 empty] | Environment
| SO2 (g per GJ fuel) | For electric heating, the emissions depend on how the electricity is produced. Emission factors for electricity in Denmark can for instance be found in socioeconomic assumptions for energy projects published by the Danish Energy Authority (www.ens.dk). | [9 empty] | SO2 (g per GJ fuel) | For electric heating, the emissions depend on how the electricity is produced. Emission factors for electricity in Denmark can for instance be found in socioeconomic assumptions for energy projects published by the Danish Energy Authority (www.ens.dk).
| NOX (g per GJ fuel) | [10 empty] | NOX (g per GJ fuel)
| CH4 (g per GJ fuel) | [10 empty] | CH4 (g per GJ fuel)
| N2O (g per GJ fuel) | [10 empty] | N2O (g per GJ fuel)
| Particles (g per GJ fuel) | [10 empty] | Particles (g per GJ fuel)
| Financial data | [10 empty] | Financial data
| Specific investment (1000€/unit) | 3 | 2.9257 | 2.7827 | 2.5173 | 2.4 | 3.3 | 2.0138 | 2.769 | D, E, F | 4 | Specific investment (1000€/unit) | 106 | 103.3764 | 98.3223 | 88.9434 | 84.8 | 116.6 | 71.1547 | 97.8377 | D, E, F | 4
| - hereof equipment (%) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 4 | - hereof equipment (%) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 4
| - hereof installation (%) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 4 | - hereof installation (%) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 4
| Possible additional specific investment (1000€/unit) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Possible additional specific investment (1000€/unit) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fixed O&M (€/unit/year) | 25 | 24.3812 | 23.1892 | 20.9772 | 20 | 40 | 15 | 30 | C, E |  | Fixed O&M (€/unit/year) | 50 | 48.7624 | 46.3784 | 41.9544 | 40 | 80 | 30 | 60 | C, E
| Variable O&M (€/MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Variable O&M (€/MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Technology specific data | [10 empty] | Technology specific data
References:
4 | Peter Strøm from “EL-Strøm A/S”, personnaly communication.
Notes:
A | Annual efficiency based on 100 % space heating efficiency and hot water efficiency. In addition, distribution heat losses compared to water based heating systems are saved, typically in the range of 5-10 %.
B | Assuming 150 apartments.
C | Assuming change of heating elements in the hot water tank every 10 years.
D | The price includes the complete system including room heaters and hot tap water preparation.
E | Assuming a cost-reduction of 0.5 % p.a., which in turn is assumed equivalent to the typical improvement of mature technologies.
F | Including costs of wiring and procurement and installation of radiators

## 217 SOFC mCHP - n. gas & biogas
| Technology | SOFC (microCHP) - natural gas / biogas One-family house existing and new building
|  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
| Heat generation capacity for one unit (kW) | 0.66957 | 0.56 | 0.56 | 0.56 |  |  |  |  | A
| Electricity generation capacity for one unit (kW) | 0.7 | 0.7 | 0.7 | 0.7 |  |  |  |  | B
| Typical share of space heating demand covered by unit (%) | 0.11208 | 0.075556 | 0.075556 | 0.075556 |  |  |  |  | A
| Typical share of hot tap water demand covered by unit (%) | 1 | 1 | 1 | 1 |  |  |  |  | A
| Electric efficiency, annual average, net (%) | 46 | 50 | 50 | 50 | 46 | 57 | 48 | 60 | C | 20
| Heat efficiency, annual average, net (%) | 44 | 40 | 40 | 40 |  |  |  |  | C, J
| Total efficiency, annual average, net (%) | 90 | 90 | 90 | 90 |  |  |  |  | C
| Auxiliary Electricity consumption (kWh/year) | - | - | - | -
| Technical lifetime (years) | 10 | 20 | 20 | 20 |  |  |  |  | D
Regulation ability
Primary regulation (% per 30 seconds)
Secondary regulation (% per minute)
| Minimum load (% of full load) | 0.7 | 0.7 | 0.7 | 0.7
| Warm start-up time (minutes) | 1.5 | 1.5 | 1.5 | 1.5
| Cold start-up time (minutes) | 360 | 240 | 240 | 240 |  |  |  |  | E
Environment
| SO2 (g per GJ fuel) | 0 | 0 | 0 | 0
| NOX (g per GJ fuel) | NA | 2 | 2 | 2
| CH4 (g per GJ fuel) | NA | 1.25 | 1.25 | 1.25
| N2O (g per GJ fuel) | NA | 0 | 0 | 0
| Particles (g per GJ fuel) | 0 | 0 | 0 | 0
Financial data
| Specific investment (1000€/unit) | 27 | 21 | 16 | 11 | 17 | 27 | 5 | 16 | F, G | 18, 21
| - hereof equipment (%) | 80 | 80 | 80 | 80
| - hereof installation (%) | 20 | 20 | 20 | 20
| Fixed O&M (€/unit/year) | 1350 | 1050 | 800 | 550 |  |  |  |  | I | 19
| Variable O&M (€/GJ) | 0 | 0 | 0 | 0
Technology specific data
References:
[18] | Contini, V., Eubanks, F. & Jansen, M., Stationary and Emerging Market Fuel Cell System Cost Analysis - Auxiliary Power Units, Batelle, 06/19/2014, Washington D.C.
[19] | Technology Roadmap - Hydrogen and Fuel Cells, 2015, International Energy Agency
[20] | Pacific Northwest National Laboratory, New small solid oxide fuel cell reaches record efficiency, 2012, http://www.pnnl.gov/news/release.aspx?id=926
[21] | The cost of domestic fuel cell micro-CHP systems, London Business School, https://spiral.imperial.ac.uk/bitstream/10044/1/9844/2/The%20cost%20of%20domestic%20fuel%20cell%20micro-CHP%20systems%20(ICBS%20format).pdf
Notes:
A | The heat output is 0.6 kW. The system is also combined with a peak demand boiler (up to 25 kW thermal power), this is to match the heat demand for a household. The value presented in the table does not include the contribution from a peak demand boiler. Assumed 6000 full loads hours per annum for fuel cell. Assumed that supplying hot tap water is given priority.
B | The electrical output of this system is up to 0.7 kW, but varies between 0.2 – 5 kW when evaluating European and Japanese systems. [1,7,11, 13-15]
C | Looking at listed values for more manufacturers the electrical efficiency ranges from 35 to 60 %. Large variations in the electrical / heat efficiency as different manufacturers run their units in different modes, e.g. optimized for either heat or power production. Heat efficiency increases as the electrical efficiency decreases. Heat efficiency refer to the SOFC micro CHP alone, e.g. any production from peak demand boiler is excluded as this differs between different technologies.
D | The techno economical lifetime is the lifetime of the whole system. The stack lifetime is shorter and the stack is expected to be exchanged during this period. The stack life-time is expected to be app. 10 years in 2020 [5].
E | Start up from an outdoor or room temperature is slow as the units contain ceramics. If the system is at operating temperature the stack can be started faster, assuming that gases are supplied and help systems are active. Also shut down can be performed quickly, not counting in the time required to cool the system.
F | Price in Japan 19,400 Euro. Cost of modification for European market plus installation is estimated by DGC to add up to 27,000 Euro/unit
G | The specific investments for 2020, 2030 and 2050 are estimated from [16]. The major price reduction factor between 2020 and 2050 is mass production of units (50,000 units/year assumed in 2050).
H | The uncertainties for specific investment costs reflect variations in the level of mass production based on figures given in [16].
I | Fixed O&M costs assumed to be 5% of the specific investment based on [17]. In [17], the fixed O&M is estimated to be 5% of investment for Alkaline and PEM FC. The same is assumed for SOFC.
J | The heat efficiency, which can be derived, depends on the return temperature of the cooling circuit and the size of the heat exchanger.

## 218 LT-PEMFC mCHP - hydrogen
| Technology | LT-PEMFC (microCHP) - hydrogen
|  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
| Heat generation capacity for one unit (kW) | 0.77778 | 0.7 | 0.7 | 0.7 |  |  |  |  | A, B
| Electricity generation capacity for one unit (kW) | 0.7 | 0.7 | 0.7 | 0.7 |  |  |  |  | A
| Typical share of space heating demand covered by unit (%) | 0.14815 | 0.12222 | 0.12222 | 0.12222 | 20 | 70 | 20 | 70 | B
| Typical share of hot tap water demand covered by unit (%) | 1 | 1 | 1 | 1 |  |  |  |  | B
| Electric efficiency, annual average, net (%) | 45 | 47 | 50 | 50 |  |  |  |  | C
| Heat efficiency, annual average, net (%) | 50 | 47 | 46 | 48 |  |  |  |  | C, I
| Total efficiency, annual average, net (%) | 94 | 94 | 96 | 98
Auxiliary Electricity consumption (kWh/year)
| Technical lifetime (years) | 7 | 10 | 20 | 20 |  |  |  |  | D
Regulation ability
Primary regulation (% per 30 seconds)
Secondary regulation (% per minute)
Minimum load (% of full load)
| Warm start-up time (minutes) | 2 | 2 | 2 | 2
| Cold start-up time (minutes) | 2 | 2 | 2 | 2 |  |  |  |  | E
Environment
| SO2 (g per GJ fuel) | 0 | 0 | 0 | 0
| NOX (g per GJ fuel) | 0 | 0 | 0 | 0
| CH4 (g per GJ fuel) | 0 | 0 | 0 | 0
| N2O (g per GJ fuel) | 0 | 0 | 0 | 0
| Particles (g per GJ fuel) | 0 | 0 | 0 | 0
Financial data
| Specific investment (1000€/unit) | 11.7 | 11 | 8 | 6 | 9 | 13 | 4 | 10 | B, I | 6, 9, 11
| - hereof equipment (%) | 71 | 64 | 48 | 50 |  |  |  |  | H
| - hereof installation (%) | 29 | 36 | 52 | 50 |  |  |  |  | F
| Fixed O&M (€/unit/year) | 700 | 700 | 500 | 400 | 600 | 1300 | 200 | 1000 | D, G, J | *
| Variable O&M (€/GJ) | 0 | 0 | 0 | 0
Technology specific data
| Shut down time (minutes) | 0.1 | 0.1 | 0.1 | 0.1
References:
[6] | Wei, Max et al., A Total Cost of Ownership Model for Low Temperature PEM Fuel Cells in Combined Heat and Power and Backup Power Applications, Lawrence Berkeley National Laboratory, University of California Berkeley, Environmental Energy Technologies Division, October 2014
[9] | Aki MARUTA, 2016. Technova Inc . Japan’ s ENE-FARM programme. https://www.energyagency.at/fileadmin/dam/pdf/projekte/gebaeude/Maruta.pdf, accessed 17.08.2017.
[11] | International Energy Agency, 2015, Technology Roadmap - Hydrogen and Fuel Cells
* | An asterisk in the reference indicate high uncertainty or "guesstimate", where more certain data was not available
Notes:
A | A µCHP is up to 5 kWAC in power
B | An additional heating device is not considered, but probably necessary for older heat demanding buildings. A combined heat storage and 15 kW electrical boiler will increase the equipment cost of 1,300 € (2015). Several ‘plug & play’ boilers are available, the increase in installation cost will only be marginal, Assumed 6000 full loads hours per annum for the fuel cell. Assumed that supplying hot tap water is given priority.
C | A degradation rate of 3.5 µV/h has been proven in the Danish µCHP project. This indicates a technical stack lifetime of 20,000 operational hours (10% voltage decay). The degradation rate of 3.5 µV/h (corresponding to 0.5% per 1,000 h's) will result in an electrical efficiency loss of 5% over 20,000 hours. A BoL electrical efficiency of 47% has been proven by DGC in the Danish µCHP-project. An average electrical efficiency over the 20,000 h' is entered. The loss in electrical efficiency is converted to heat! A BoL heat efficiency of 47% has been measured by DGC in the Danish µCHP-project. The heat efficiency is also entered as an average lifetime efficiency (2015). (The latest IRD µCHP is 50% electrical and 41% heat efficient at BoL), please note that increased electrical efficiency is obtained on behalf of heat efficiency)
D | One stack exchange is included in the O&M for 2015. The official Danish heating season is 1-oct to 30-apr (5,064 h's). The summer operation (5 month per year) includes only domestic hot water production, which typically is 2,500 kWh/year per family. The accumulated need for domestic hot water during the summer month is therefore around 1,050 kWh and will be covered by 1,050 operational hours with the µCHP. The estimate yearly operation is therefore considered to be around 6,100 h's given the SoA stack a lifetime of 3-4 years.
E | Proven in the Danish µCHP-project. For the post-2015 µCHP versions a supercapacitors or batteries will be included (fast start-up as UPS-systems)
F | Based on the installation cost in the Danish µCHP project
G | Assuming one annual service inspection
H | The decrease of equipment cost is closely linked to the production volume. The estimated price development is inspired by the learning curves from the ENE-FARM 'project cf. Fig. 17.4 [Ref. 1-2] and the results of the recent Delta-ee survey cf. Fig. 13.5 [Ref. 3-4]. The latter has concluded that over two-thirds of European homeowners would be willing to invest in µCHP, following a survey carried out in the UK, Germany and the Netherlands, but the price would have to be halved. Delta-ee furthermore concluded that householders are willing to pay a premium price for fuel cell µCHP over engine-based - but just how much of a premium varies by country (cf. Fig. 17.5)
I | 2015 pries is based on today's prices observed in Japan for systems using natural gas as input. We assume a cost reduction of EUR 2000 to account for the cost of the reformer. Installation cost are estimate to be EUR 1000 (higher in demonstration projects). Estimation of uncertainties for specific investment costs based on [5].
J | See section 'Uncertainty' for FC-LT PEM microCHP hydrogen.
K | The heat efficiency, which can be derived, depends on the return temperature of the cooling circuit and the size of the heat exchanger.

## 219 LT-PEMFC mCHP - natural gas
| Technology | LT-PEMFC (mCHP) - methane/natural gas
|  | 2015 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
| Heat production capacity for one unit (kW) | 1.2035 | 1.1946 | 1.2145 | 1.2145 |  |  |  |  | A | 8
| Electricity generation capacity for one unit (kW) | 0.7 | 0.7 | 0.7 | 0.7 | [5 empty] | 8
| Typical share of space heating demand covered by unit (%) | 0.29006 | 0.28708 | 0.29373 | 0.29373 |  |  |  |  | J
| Typical share of hot tap water demand covered by unit (%) | 1 | 1 | 1 | 1 |  |  |  |  | J
| Electric efficiency, annual average, net (%) | 34.2 | 35.1 | 35.1 | 35.1 | 31 | 39 | 31 | 39 | G | 8, 13
| Heat efficiency, annual average, net (%) | 58.8 | 59.9 | 60.9 | 60.9 |  |  |  |  | I | 8
| Total efficiency, annual average, net (%) | 93 | 95 | 96 | 96 | [5 empty] | 8
| Auxiliary Electricity consumption (kWh/year) | - | - | - | -
| Technical lifetime (years) | 20 | 20 | 20 | 20 |  |  |  |  | B | 8
Regulation ability
Primary regulation (% per 30 seconds)
Secondary regulation (% per minute)
Minimum load (% of full load)
| Warm start-up time (minutes) | 7 | 5 | 5 | 5 |  |  |  |  | E | 9
| Cold start-up time (minutes) | 45 | 40 | 30 | 30 |  |  |  |  | E | 9
Environment
| SO2 (g per GJ fuel) | 0 | 0 | 0 | 0 |  |  |  |  | C | 11
| NOX (g per GJ fuel) | 2 | 2 | 2 | 2 | [5 empty] | 11
| CH4 (g per GJ fuel) | 2 | 2 | 2 | 2 | [5 empty] | 12
| N2O (g per GJ fuel) | 0 | 0 | 0 | 0
| Particles (g per GJ fuel) | 0 | 0 | 0 | 0 | [5 empty] | 11
Financial data
| Specific investment (1000€/unit) | 13.7 | 12 | 9 | 7 | 10 | 14 | 5 | 11 | D, F | 2
| - hereof equipment (%) | 68 | 67 | 65 | 60 |  |  |  |  | D
| - hereof installation (%) | 32 | 33 | 35 | 40 |  |  |  |  | D
| Fixed O&M (€/unit/year) | 800 | 800 | 550 | 450 | 350 | 1000 | 250 | 800 | H | 10, *
| Variable O&M (€/GJ) | - | - | - | -
Technology specific data
| Shut down time (minutes) | 5 | 5 | 5 | 5 | [5 empty] | 9
References:
[2] | Wei, Max et al., A Total Cost of Ownership Model for Low Temperature PEM Fuel Cells in Combined Heat and Power and Backup Power Applications, Lawrence Berkeley National Laboratory, University of California Berkeley, Environmental Energy Technologies Division, October 2014
[8] | Toshiba Japan in IEA Annex 25 presentation Oct. 2014
[9] | No data available from Toshiba. Results from tests of Dantherm Power µCHP in the project "Dansk Mikrokraftvarme”
[10] | Maintenance cycle 3,5 years specified from Toshiba for 2014
[11] | EUR 20681 Rapport, 2003/2010 "Fuel Cells"
[12] | Lowest value found in www.asue.de
[13] | Technology Roadmap - Hydrogen and Fuel Cells, 2015, International Energy Agency
* | An asterisk in the reference indicate high uncertainty or "guesstimate", where more certain data was not available
Notes:
A | Without peak load boiler, however a condensing peek boiler is included in the cost considerations
B | Stack lifetime specified for 80.000h by Toshiba
C | Fuel cleaned for sulphur to avoid damage of fuel cell system
D | Estimate based on price in Japan by Panasonic/Tokyo Gas 1.630.000YEN in 2016 (=€12.700). To this is added €1000 in installation cost (may be higher for the first units or demonstration projects) . The European market requires installation indoor and adoption to a different gas and power quality. The European requirements results in higher cost than in Japan. The cost reduction is estimated based on increased integration and increased volume advantages. Introduction costs in the European market can be expected to be significantly higher, approx. €20,000 by 2017.
E | Up/down regulation will vary with seasonal heat load
F | Estimation of uncertainties for specific investment costs based on [6].
G | Uncertainties for electric efficiencies estimated from [6]. Efficiency takes into account, a 20 % drop in electrical efficiency during the life-time of the fuel-cell.
H | See section 'Uncertainty' for FC-LT PEM microCHP natural gas.
I | The heat efficiency, which can be derived, depends on the return temperature of the cooling circuit and the size of the heat exchanger.
J | Assumed 6000 full loads hours per annum. Assumed that supplying hot tap water is given priority.